# VOLUME 3

# TECHNICAL SPECIFICATIONS

CONTENT

PREAMBLE TO SPECIFICATION	……………………………………………..3

Part 1 – WTP Majdevo ……………………………………………….…...4

A. TECHNICAL DESCRIPTION …………………………….……………….4

- GENERAL TECHNICAL CONDITIONS …………………………........43

Part 2 – CCMS …………………………………………………………..…..97

- HYDRAULIC AND CIVIL ENGINEERING PART ………………..….…97

B. MECHANICAL PART  ……………………………………………..……150

C. 	ELECTRICAL DESIGN ………………………………….……….……...203

Part 3: TM to Cicevac and Varvarin ………………………….……290

A) TECHNICAL DESCRIPTION ………………………………………….……290

B) GENERAL TECHNICAL CONDITIONS …………………………….……..298

# PREAMBLE TO SPECIFICATION

This section of the Tender Documentation comprises the Technical Specifications for the Contract TD “Rasina District: Regional Water Supply Project that is being financed by the Delegation of the European Commission to the Republic of Serbia

through the IPA 2008 programme.  Beneficiary of the project is the Municipality of Krusevac.

The Conditions of Contract, the Technical Specifications, the Drawings and the Bill of Quantities are to be read in conjunction with each other but in the order of precedence as stipulated in Contract Agreement.

Notwithstanding the subdivision of the Specification under different headings, every part of it shall be deemed supplementary to and complementary to every other part.

The headings in the Specification shall not be deemed to be part thereof or be taken into consideration in the interpretation of the Contract.

All references made in the Specification will be references to Clauses or sub-Clauses hereof, unless specified otherwise.

The works are as described in the Invitation to Tender and the Contractor will be deemed to have entered rates in the Bill of Quantities to cover all the requirements set out in these Specifications.  No other payments will be allowed.

The Specification shall not be considered as being exhaustive and the Tenderer will be deemed to have included all necessary plant and equipment whether specified or not.

Part 1 – WTP Majdevo

A. TECHNICAL DESCRIPTION

- INTRODUCTION

The water treatment plant (WTP) in Majdevo was built in 1984 with a treatment capacity of 650l/s.  It currently treats 400l/s of water during the winter and up to 600l/s in the summer. The WTP capacity available today meets the public demand of the City of Kruševac but since the city’s water distribution network will be expanded to include the municipalities of Aleksandrovac, Varvarin, Ćićevac and, in part, Trstenik, the WTP capacity has to be increased.

The general (conceptual) design for the reconstruction and expansion of the Majdevo WTP at its current location calls for the reconstruction of the existing plant and the addition of new structures which will increase plant capacity to 1000 l/s and ensure that the quality of the water delivered by the WTP meets the criteria prescribed in the Book of Regulations on Hygienic Safety of Drinking Water.

The capacity of the existing plant will be increased with minimal additional construction of process units and re-construction of existing structures (such as filters, the ozonation station and the sedimentation station), while ensuring both the maximum capacity and maximum quality of delivered water.

The key parameters of the plant’s treatment process have been analyzed, the condition of the existing equipment has been assessed, potential operating problems have been identified, and a new water treatment process has been proposed, including:

- sedimentation, with the addition of polyelectrolyte at the coagulation and flocculation stage and sedimentation in a super pulsator;

- ozonation,

- filtration at dual-layer (sand/anthracite) filters,

- chlorine disinfection.

2.	PRESENT CONDITION OF THE PLANT

Water is delivered to the WTP from the Ćelije Reservoir via a DN 1000, 2915 m-long pipeline.

The WTP is comprised of the following components:

- Regulation station

- Flow meter

- Lime dispensing unit

- Aluminium sulfate dispensing unit

- Pulsator

- Ozonation station

- Sand filtration station

- Treated water tank

  - Dispensing of coagulant and distribution chamber

The current clarification process begins with the addition of aluminium sulfate or PAC and polyelectrolyte directly into the pipeline and the distribution chamber, to initiate the coagulation/

flocculation process.

Chemicals are currently dispensed at the DN 1000 raw water pipeline.

The DN 1000 pipeline delivers water to the settling chamber where water is distributed and aluminium sulfate dispensed.  The water level in the settling chamber is at 253.50 m above sea level.

Only two chambers are active at present, from which the water is transferred to the sedimentation tank/pulsator via a DN 550 pipeline.  The water level in the discharge units of the distribution chamber is at 252.37 m a.s.l.

2.2.  Pulsator

From the distribution chamber, the water is transferred directly into two sedimentation units/pulsators which operate as ordinary clarifiers sized for a capacity of 350 l/s, including vertical flow and sludge cloud.

The technical characteristics of these units are:

- Size: 		length	 24.3 m

width	 15.6 m

depth - bottom – pipe openings 4.4 m

- Useful volume: 	V  1600 m3

Each sedimentation unit features separate zones for:

- mixing of raw water with flocculant,

- flocculation, creating contact between new flakes and previously separated sludge; and

- clarifying.

Water is delivered to pontoons by means of a DN 550 2.3x2.3m pipeline and from there to DN 300 pipes via a channel (2.3x0.6m, 10.5m long).  Twelve perforated DN 300 pipes, connected to the channel, deliver water to the pulsator.  Water orientation units are installed in the DN 300 pipeline.

The current flow rate to the pulsators is roughly Q=650l/s=2340m3/h, resulting in the following parameters:

- Contact time: t = 82 min = 1 h 22min

- Entrance velocity: 5.4 cm/min = 3.2 m/h

- Amount of separated sludge: 300 m3/day  0.87 %

In order to alleviate current pulsator problems, a unit for the separation of coagulation and flocculation processes prior to the transfer of water to the pulsator should be added.

2.3.	Ozonation station

After leaving the sedimentation tank, water is conveyed to the ozonation station through a 1.4m-wide concrete channel. The ozonation facility consists of two separate lines, only one of which is in operation. The facility consists of:

- an engineering room, in which equipment is installed

- a tank with chambers for ozone introduction and the ozonation process.

The following are installed in the engineering room:

- two ozone generators of 5.0 kg/O3/h capacity, one operating and one backup unit

- an ozone destructor

- pneumatic drive compressors

The ozonation equipment was installed in 1980; as such, it is outdated and worn. Ozone generators produce ozone from the air so that in addition to the ozone generators, there are high-pressure compressors - air driers. The ozone generators do not operate at a capacity of 5.0 kg/O3/h but with considerably lower capacity. Two additional locations are available in the engineering room for the installation of the ozone generators which are to be used during the second phase.

The ozone destructor is not in operation.

Atlas Copco GA 30 high-pressure compressors for compressed air are operational.

The introduction of ozone into the water is carried out in both the ozonation chambers through pipe systems.

2.4.	Filtration

Following ozonation, the water is conveyed to gravity filters via a 1.4 m-wide channel.  Existing filters are dual-bottom gravity sand filters. Filtration can be controlled from the Control Center or from a panel near the filters.

Water to be filtered is delivered to a central location and this leads to a number of filter operation problems:

- The delivery of water disturbs the surface of the filter filling, especially after cleaning of the filters.

- Uneven distribution of water by filter field and, consequently, an uneven filter load.

At the filtration station, there is no adequate air ventilation and the filters are not protected from  direct sunlight.

2.5.	Pipe gallery

A pipe gallery is located adjacent to the sand filters.  The treated water tank is beneath the pipe gallery.  All pipes are made of steel and the flange-fitted butterfly valves are electrically-driven.

The pipe gallery includes pipes for:

- the supply of filter backwash water, DN 400

- the supply of filter scouring air, DN 200

- the discharge of treated water, DN 250

The DN 250 treated water pipe is connected at the DN 500 backwash water supply pipe and leads directly to the treated water tank.

All pipes and valves are more than 20 years old, rather worn and corroded.  They have to be replaced.

2.6.	Pumping stations and engineering room

The engineering room contains:

- Filter-cleaning pumps

- Filter-cleaning compressors

- Pumps discharging water to Nabrđe

- Pumps discharging water to Majdevo

- Pumps discharging water to Aleksandrovac

- Pumps for WTP’s internal water supply.

2.7.	Controls and electrical installations

Of all the existing equipment at the Majdevo WTP, the condition of the measuring instruments, regulation equipment, and controls is worst, not only because after 20 years many of these are no longer operational, but also because the equipment is generally obsolete.

The Control Center (CC) is located on the upper floor of the administration building and is comprised of a control panel and a synoptic display which contains a layout of the water treatment process and shows the functions of individual WTP equipment components.

Power supply to the Majdevo WTP is provided by two above-ground 10kV power lines running from two independent transformer stations. From the end posts equipped with overhead lines and insulators, the power is supplied to the existing transformer station TS 10/0.4 kV via 10kV underground cabling.

The transformers are 630kVA oil transformers located in special transformer bays.  One is in operation and the other is a »cold« backup unit.

10kV and 0.4kV switchgear substations are comprised of free-standing cells and located in a common room.

The 10kV (=1K) switchgear substation is made up of 8 cells (2 transformer cells, 1 measurement cell, 4 switchboard cells, and 1 backup cell). The low-voltage 0.4kV switchgear substation (=1NE) is comprised of 7 cells (2 transformer cells, 1 external lighting cell, 1 reactive energy compensation cell and 3 distribution cells).

Consumers are connected by means of cables running in cable trenches in the floor beneath.

Power consumption is measured by means of a HV power measurement group located on the wall of the switchgear substation room.

### 2.8	Backup power supply

A 185 kVA diesel electric power pack is used as a backup power supply unit for priority consumers.  It is located in a separate room adjacent to the transformer station.  The diesel power pack starts automatically upon grid power outage.  The grid/diesel cabinet (=1U) is a free-standing cabinet and is located in the diesel power pack room.

3.	RECONSTRUCTION OF THE WTP

The design calls for the reconstruction of the existing plant and the addition of new structures which will increase plant capacity to 1000 l/s and ensure that the quality of the water delivered by the WTP meets the criteria prescribed in the Book of Regulations on Hygienic Safety of Drinking Water.

The capacity of the existing plant will be increased with minimal additional construction of process units and re-construction of existing structures (such as filters, the ozonation station and the sedimentation station), while ensuring both the maximum capacity and maximum quality of  delivered water.

The capacity of the WTP is 1000 l/s but its structural components have been designed such that they are comprised of two lines of 500 l/s capacity each.  All treatment lines can be inter-connected by means of pipes. The structural components have been designed so that they line up in the downstream direction and constitute a logical assemblage with the shortest possible connecting pipes.

The first structural component of the WTP is the distribution chamber whose function is to receive water from the dam and distribute it to two coagulation and flocculation lines.  No polyelectrolyte is dispensed into the distribution chamber.

The water will be conveyed to two new coagulation and flocculation structures, where polyelectrolyte will be dispensed.  The coagulation and flocculation process will take place in two chambers with agitators, and then the water will be transferred to the reconstructed pulsator for sedimentation.  Settling plates will be incorporated into the pulsator.

Following sedimentation, the water will be ozonated.  Two new ozone generators will be installed and the ozonation chamber reconstructed.

The filtration station is the third structural component of the process line.  It is comprised of:

- A filtration station with 8 filters; and

- A pipe gallery.

Existing sand filters will be reconstructed as follows:

- The filter filling will be replaced with sand and anthracite filling.

- Overflow channels will be installed to transfer water to the filters.

- The pipe gallery will be reconstructed.

The filter filling is backwashed and air scoured.  Existing backwash water pumps do not currently provide sufficient capacity so both the pumps and the backwash water supply piping will be replaced.

3.1.	Clarifying

A coagulation and flocculation unit will be provided, before water enters the sedimentation facility.  The general design calls for:

- Construction of a new coagulation and flocculation unit in the area adjacent to the distribution chamber and above the pulsator unit; and

- Reconstruction of the existing pulsator, including the incorporation of settling plates into the pulsator and conversion to a super pulsator.

Water is conveyed to the settling chamber (via a DN 1000 pipe), where it is distributed and aluminium sulfate is dispensed.  The water level in the settling chamber is at 253.50 m a.s.l.

The new structure will have two independent lines, with a maximum capacity of 500 l/s each. Each line will have two chambers equipped with suitable agitators for slow mixing along the entire surface and depth of the chamber.  Chamber characteristics are as follows:

- First chamber:

- Number of in-line chambers .........1

- Chamber volume: .......................150 m3

- Contact time:.............................. 5 min

- Second chamber:

- Number of in-line chambers ..........1

- Chamber volume: ....................... 360 m3

- Contact time:.............................. 12 min.

The last structural component of the series of flocculation chambers is a room which will accommodate a polyelectrolyte preparation and dispensing unit.

Water which is well mixed with aluminium sulfate dispensed into the settling chamber, enters the flocculation chambers. Initial flocs are formed in the DN700/DN800 pipes which convey the water from the settling chamber to the flocculation unit.

The ancillary flocculant – polyelectrolyte – is dispensed at the first flocculation stage to accelerate the increase in floc size.  At the second flocculation stage, a proper agitation speed is selected and the flocculation process completed such that the flocs are ready for the sedimentation process.

Flocculator 1 has a 200 stainless-steel shaft and a 2980 mm impeller blade.  The agitator speed (min-max) is 2 – 10 min-1 and the power of the agitator is 1.1 kW. Stainless steel blenders, bearings and a buncher with a dual-gear reducer are mounted on the stainless steel structure.

Flocculator 2 has a 200 stainless steel shaft and a 4250 mm impeller blade.  The agitator speed (min-max) is 0.5 – 3 min-1 and the power of the agitator is 0.75 kW. Stainless steel blenders, bearings and a buncher with a dual-gear reducer are mounted on the stainless steel structure.

There are two pipes, DN 700 and DN 800, running from the settling chamber, which covey water to the flocculation chambers.  The pipe running to the closer flocculation line is DN 700, while the one running to the other flocculation line is DN 800 due to higher losses.  Two manholes will be built in the area between the super pulsator and the flocculation unit, which will accommodate valves that will direct the water to the flocculation unit or directly to the super pulsator.

Water will be conveyed to the first flocculation chamber via a DN 700 pipe and will enter from above, and then from there, below the partition for the dispensing of polyelectrolyte, it will enter the second flocculation chamber from underneath. Water will be discharged from the second flocculation chamber from above, via a DN 700 pipe, to the super pulsator.

The following components will be installed in the first manhole toward the first flocculation line:

- A manually-driven butterfly valve, DN 700, and dismantling piece, DN 700, on the DN 700 pipe which will convey water to the first flocculation chamber;

- A manually-driven butterfly valve, DN 700, and a dismantling piece, DN 700, on the DN 700 pipe which will return water from the second flocculation chamber to the super pulsator; and

- A manually-driven butterfly valve, DN 700, and a dismantling piece, DN 700, on a DN 700 pipe between the pipes running to and from the flocculation unit.  This valve will be closed during regular operation of the system, and opened only when the water needs to be conveyed from the settling chamber directly to the super pulsator (if a flocculation line is not in service).

For engineering reasons, the flocculation chambers on the second flocculation line will be turned relative to the flow of water, such that the water supply pipe DN 800 will be at a 90-degree angle toward the flocculation chambers.

The following components will be installed in the second manhole on the second flocculation line:

- A manually-driven butterfly valve, DN 800, and dismantling piece, DN 800, on a DN 800 pipe which will convey water to the first flocculation chamber;

- A manually-driven butterfly valve, DN 800, and a dismantling piece, DN 800, on a DN 800 pipe which will return water from the second flocculation chamber to the super pulsator; and

- A manually-driven butterfly valve, DN 800, and a dismantling piece, DN 800, on a DN 800 pipe between the pipes running to and from the flocculation facility. This valve will be normally closed, and opened only when the water will have to be conveyed from the settling chamber directly to the super pulsator (if a flocculation line is not in service).

The current inlet into the super pulsator is DN 500 and will remain unchanged because the pipe is already beneath the structure and enters the plant from underneath.  DN 700 or DN 800 pipes running from the flocculation unit will be reduced and connected with the DN 500 pipe.

3.1.1 Super pulsator

In order to enhance the sedimentation process, the existing pulsators will be reconstructed and transformed into a super pulsator (sedimentation tank with settling plates).

Existing DN 200 perforated pipes, which discharge water following sedimentation, will be dismantled and settling plates and collection channels for clarified water will be installed instead.

The settling plates will be made from stainless steel and will have the following characteristics:

- Width						0.9 m

- Length 						1.54 m

- Thickness					1 mm

- Inclination					55

- Distance between plates			8 cm

- Number of plates per pulsator			3500

Clarified water discharge channels will be attached to the collection channels, which convey water to the ozonation station, in places where the perforated pipes are currently attached.  One super pulsator line will have 12 clarified water discharge channels (30 cm wide and 50 cm high).  The channels will be made from stainless steel, about 5 mm thick, and the support structure will be a 1.2 m-high „H“ piece with appropriate reinforcements and settling-plate support frames.  The support channel (structure) will rest on stainless-steel posts, DN 200, about 4 m high, in two places between the wall and the collection channel (1.7 m).

Between the channels there is a 90 cm-wide area where the settling plates will be installed.  The plates will be spaced 8 cm apart and suspended from metal frames (channel supports).  Channels are attached at one end to concrete collection channels which discharge water to the ozonation unit, and to the concrete wall at the other end.  This design facilitates the removal and cleaning of settling plates.

Existing sludge evacuation pipes will be replaced because they are worn and substantially corroded.  The sludge evacuation system will not be replaced (i.e., the concrete channels for sludge evacuation and the evacuation unit will be retained).

The design does not call for the replacement of water supply pipes to the super pulsator.

This will yield two modern super pulsators with the following operating characteristics:

- Type:			pulsator/sedimentation tank with settling plates

- Number of units: 	2

- Size:			length	 24,3 m

width	 15,6 m

depth – bottom – overflow edge of collection channels 4.5 m

- Useful volume 		V = 1650 m3

- Discharge 		Q = 950 l/s = 3420 m3/h

- Contact time 		ts = 0.96 h = 58 min

- Entrance velocity 	7.7 cm/min  4.6 m/h

- Upper-zone settling plates to a depth of 1.2 m are spaced 8 cm apart and at an angle of 55

- Computed surface load (i.e., flow velocity through a settling plate)

- Computed equivalent sedimentation surface following insertion of settling plates

3.1.2 Preparation and dispensing of polyelectrolyte

The design calls for a maximum concentration of 0.2 mg/l. For a total capacity of 1000 l/s of the Majdevo WTP, a unit whose maximum capacity is 1000 l/h has been selected.  It operates as follows:  The polyelectrolyte is fed from a storage container into the dispensing unit, mixed with a pre-defined amount of water, and released into a chamber equipped with a mixer where the solution is prepared.  Following preparation, the polyelectrolyte solution is conveyed to a dispersion chamber with a mixer and from there to the polyelectrolyte solution curing and dispensing chamber.

The concentration of the flocculant in the solution can be controlled in two ways:  either by adjusting the water flow or by controlling the dispensing of the polyelectrolyte.  When the content in the curing/dispensing chamber reaches a set level, the supply of water and polyelectrolyte is automatically restarted and stopped when the chamber is full.  Sensors are automated and protect the dispensing pump.

3.2.	Dispensing of chemicals

The future treatment concept should ensure, above all, that appropriate measures are applied to provide regulated sanitary protection of the watershed and the Ćelije reservoir. This includes the treatment of wastewater originating from Brus and Blace, the necessary erosion control measures applied within the watershed, and the establishment of an immediate sanitary zone within the reservoir.

3.2.1 Dispensing of ClO2

ClO2 should be dispensed in concentrations of 0.05 mg/l. This chlorine dioxide concentration has been determined to be sufficient for preliminary disinfection. Calculations of the required amount of solution should be based on a capacity of 1000 l/s and a concentration of 0.05 mg/l.

Two units of 100 gr/h each have been selected (daily consumption, if 4.32 kg/day is dispensed continuously). The concentration of the basic solution is 3 kg/m3, meaning that the daily amount is 1.44 m3.

An estimate of the ClO2 rate of consumption at the Majdevo WTP is shown in the following table for a total discharge of the Majdevo WTP of 1000 l/s.

Estimate of required ClO2 production/consumption

| Total discharge of the Majdevo WTP, l/s | 1000 |
| --- | --- |
| Maximum ClO2 dose, mg/l | 0.05 |
| ClO2 consumption, g/h | 180 |
| Solution concentration, g/l (0.3%) | 3.0 |
| ClO2 consumption, l/h | 60 |
| Daily consumption of ClO2, kg/day | 4.3 |
| Required tank volume, m3 | 1.5 |

For the Majdevo WTP in Kruševac, the design calls for a ClO2 dose of 0.05 mg/l, which translates to the required daily consumption of chlorine dioxide of 4.3 kg/day for 1000 l/s of raw water.  Based on this level of chlorine dioxide consumption at the Majdevo WTP, both conventional and advanced chlorine dioxide generation methods are acceptable.

It should be noted that the ClO2 solution will be used periodically, when KMnO4 levels exceed 8 mg/l and manganese levels exceed 0.2 mg/l.

3.2.2 Dispensing of CO2 for pH adjustment

The design calls for the dispensing of CO2 into the pipeline running from the dam, which conveys raw water to the WTP (i.e., at the current prechlorination site).

Raw water is withdrawn from the reservoir. The pipeline which transports the water to the WTP is approx. 3000 m long and its diameters are Ø 900 mm and Ø 1000 mm. Water is transported by means of gravity.  The pressure at the upstream end of the pipe, depending on the amount of water being transported, is between 1.5 and 3.5 bars (optimum level 1.6 bars). The design capacity of the WTP is 1000 l/s. The proposed point of CO2 injection is a room adjacent to the dam, through which the raw water pipeline passes. There the CO2 would be injected directly into the Ø 900 mm raw water pipeline.

A CO2 concentration of 40 mg/l has been adopted. The required dose results in the need for carbon dioxide of about 0.4 kg CO2/m3 to achieve a pH level of approximately 7.

For the adopted CO2 concentration of 40 mg/l and raw water of 1000 l/s, the required hourly consumption of carbon dioxide is:

1000 l/s x 40 mg/l x 3600 = 144 kg/h

A tank of approximately 20 m3 has been selected, to support consumption for about one week. The tank should be as close to the point of dispensing as possible, and for this reason the location of the current prechlorination station has been proposed for this purpose.

3.2.3 Flocculation unit valves and fittings

3.2.3.1 Manually-driven butterfly valves

Manually-driven butterfly valves will be installed in manholes which convey water to the flocculation unit.  These butterfly valves will be used to direct the flow of water as required.

The installation dimensions of the butterfly valves will comply with JUS (DIN) standards: JUS M.C5.005 (DIN 3202). Butterfly valve flanges will comply with JUS M.B6.011 (DIN 2503).

All valves in the supply manhole will be made from the following materials:

- Valve body			Cast alloy steel EN-JS1030

- Seat body			Austenitic CrNi steel

- Disc body 			Cast alloy steel EN-JS1030/EKB

- Rubber packing 		EPDM

- Sleeve 			Acetal

- Seal 			EPDM

- Corrosion protection	EKB epoxy coating, blue color - RAL 5015

3.2.3.2 Dismantling pieces

Dismantling pieces are used as joints and connections since they facilitate the installation of valves and pipe fittings by allowing for the adjustment of installation lengths to +/- l.

The rated pressure of flanges on dismantling pieces will be PN 10. Flange attachment dimensions will comply with JUS M.B6.011 (DIN 2503).

A dismantling flange will be comprised of: a flange, an inserted flange, and a tightening piece. Sealing will be achieved by tightening the sealing element, O-ring with the tightening piece.

The flange, inserted flange and tightening piece will be made of high-quality steel castings.

3.3.	Ozonation station

The existing ozonation station is not employed to its full extent and therefore plans call for an increase in capacity  to 1000 l/s. The station is made up of two ozonation lines and from a structural standpoint, they seem to be in good condition so that with minor reconstruction they can be used to the fullest extent possible.

The ozonation equipment is outdated and worn and, as such, the design calls for the following:

- procurement of new equipment for ozone production – ozone generators

- procurement of new equipment for ozone destruction

- procurement of new equipment for ozone introduction into water – ozone diffusers

- and procurement of appropriate equipment for measuring ozone concentration both in water and in the surrounding area, with alarm devices to ensure personnel safety.

The design calls for the installation of two ozone generators which will produce ozone from liquid oxygen.

The basic features of the ozonation station (ozonation chamber) and its equipment are:

- number of ozonation lines:		2 parallel lines, 500 l/s each

- number of chambers per line: 	2

- water depth: 				4.85 m

- volume per line:			 380 m3

- contact time: 				12.6 min, which is sufficient for the ozone 							introduction process

- ozone dosage: 			1.5 gr/m3

- maximum ozone dose in water:	3 gr/m3

- required quantity of ozone: 		GO3 = 1.0x3600x1.5 gr/m3 = 5.4 kgO3/h

- maximum quantity of ozone: 		GO3 = 1.0x3600x3.0 gr/m3 = 10.8 kgO3/h

- cooling water temperature: 		T = 15 C°

Two ozone generators of 5.4 kgO3/h capacity will have to be installed in the engineering room (dimensions 12.5 x 10.9 m).

Two catalytic ozone destructors (catalytic, with pre-heating) will also be installed.

Oil-free compressors, LFX 0.7 – 10E/50 Atlas Copco or similar, with a power level of P = 0.55 kW, will also be installed. A compressed air tank, filters, and covers will be supplied with the compressor.

To ensure regular ozone production, cooling water will be provided for the ozone generators since they will be heated to high temperatures while in operation.

Structurally, the ozonation station  consists of:

- a supply distribution channel, 1.0 x 12.5 m

- a main ozonation chamber, dimensions 5 x 6.2 m, water depth 4.85 m

- a reaction chamber, 5.0 x 6.2 m, water depth 4.85 m

- a discharge chamber, 2.4 x 12.5 m

- an engineering room where the ozonation equipment is installed (ozone generators and the catalytic ozone destructor)

Water is conveyed to a concrete distribution channel from the super pulsator via a concrete channel. Sluice gates with dimensions of 1000x1000 mm will be installed on the water inlet to the distribution chamber. Removal of the existing DN 600 gate valve and installation of a new 1000x1000 mm gate valve will reduce hydraulic losses in the water line. A gate valve must be installed and the concrete diversion barrier removed from the  water line  now being activated, in order to allow for water to be fed to the other ozonation line.

Six lines with ozone diffusers in the main ozonation chamber will need to be installed. In each chamber, 33 diffusers will be installed, through which ozone will be introduced into the water. The main chamber can be entered from the engineering room for any replacements and/or repairs of diffusers that may be needed.

From the main chamber, water is diverted under the diversion barrier into an outlet chamber in which the ozone and water reaction is carried out.

From the outlet chamber, water is fed through an overflow to the discharge chamber from which chamber water is conveyed through a concrete channel to the sand filters. An overflow of 0.5 m will be provided in the outlet chamber so as to allow for the evacuation of excess ozone.

On the concrete channel for the discharge of ozonated water to the sand filters there are two sluice gates which have corroded as a result of ozone effects over the years; these gates will be replaced. The new sluice gates will be made of  stainless steel SL 316, resistant to ozone.

On the existing ozonation line, outlet and discharge piping DN 150 is installed. On the piping for discharge from the concrete channel, a gate valve made of stainless steel is installed and a gate valve DN 150 is installed on the outlet. On the new ozonation line, an outlet and a discharge pipe with a gate valve of stainless steel will be installed.

3.3.1 Ozone production (Ozone generator)

Basic objective is that the system for water preozonation is foreseen and designed as a uniform, fully automated and monolithic ozonation system for potable water treatment with maximum flowrate of 1000 l/s = 3600 m3/h.

Ozone generator production can be automatically controlled through inlet water flow and specific ozone dosage per m3 of outlet water. Dosage is set and can be manually adjusted by plant operator depending on changes of inlet water quality. Operating capacity of ozone generator can be adjusted within operating range 10 - 100%.

For easier assembly and space saving, the entire ozone production system is divided and mounted onto two independent frames with ozone generator and power control unit, which enables easier transport, assembly and at the same time considerably reduces space needed for equipment installation.

3.3.2 Process control

Full reliability and safety in ozone production process are main objective and requirement in control of the entire process. Safety equipment for monitoring ozone concentration in ambient air includes alarm signal in case of ozone-gas leakage and automatically switches off the system with appropriate warning. In order to provide additional safety the same alarm system is used for switching on the ventilation system both in room where ozone generators are installed and in operator control room. A possibility of manual switching off the equipment from control panel in cases of emergency should also be provided.

The system is equipped with touch-panel that provides reliable operation, gives information on equipment operation and/or malfunctions (damage) and informs operator of the system on system switching on and off, process parameters and permanent monitoring.

Standard parameters controlled and adjusted (changed) on touch-panel are:

- ozone concentration in ambient air		0.00-3.00 ppm

- gas flowrate					0.0 - 150 Nm3/h

- converter power				0.0-100 kW

- cooling water temperature			0 - 100C

- consumption					0 - 100%

Each of these process parameters is monitored and analyzed for 24 h.

Ozone production equipment has own Programmable Logic Controller PLC that assures and provides independent operation of the entire system.

Control process includes direct connection (wiring) with the following system functions:

Signals from user

- external inputs/outputs

- external adjustment (4-20 mA)

Signals to user

- operational status

- information on malfunctions

- emergency stop

- information from ambient monitor

3.3.3 Ozone generator technical data

Ozone production system will automatically switch off or get in stand-by mode if there are any conditions that may cause damage of equipment or malfunction. The system shall be produced according to strict universally recognized international standards (for instance DIN 19627). The system operating principle is based on high voltage electrical discharge with thyristor-contolled frequency regulator.

Ozone generator vertically mounted, as tubular heat exchanger, with closed loop cooling system, baffle plates for cooling water circulation, equipped with high voltage electrodes (316Ti, 316L), stress free dielectric with a maximum diameter of 11mm made of high quality heat-resistant borosilicate glass. grounded tubes of the heat exchanger, the dielectric and high voltage electrodes  are centred relative to one another forming two parallel gaps where discharging takes place. Electrodes and dielectrics are made of durable borosilicate glass with minimum thickness of 1.2 mm so as to prevent dielectric failure. Replacement of electrodes is guaranteed for ten years free of charge, as necessary. High voltage electrodes directly connected to converter without fuses. Electrodes must not operate at more than 30% of rated breakdown voltage. Ozone generator equipment includes flowmeters for monitoring gas and cooling water flow, control devices for controlling cooling water temperature, as well as pressure control valves.

Basic characteristics of ozone generator are:

- number of pieces				2

- ozone production fluid				oxygen

- design capacity				5.4 kg/O3/h

- design concentration				O3

(for cooling water temperature 5C)		179 g/m3

- design concentration 			 	O3

(for cooling water temperature 25C)		148 g/m3

- operating gas pressure			1.2 bar

- outlet pressure				0.9 bar

- cooling water temperature, max		25 C

- cooling water volume				5 -10 m3/h

- required cooling water pressure		1-4 bar

- required oxygen pressure 			4-6 bar

- power supply					400 V/50 Hz/3Ph/N/PE

- materials:

- parts in contact with gas		  	304 ss/316 LSS/316 Ti

- parts in contact with cooling system	  	316 LSS/316 Gi

Space of 1.4 m around equipment is recommended for maintenance purpose.

3.3.4 Ozone generator PLC - systems

Each ozone generation unit is independent automatically controlled and equipped with own PLC, controlling simultaneously power supply system.

Basic information controlled is:

- ozone production (control of transformer, frequency and temperature regulator operation)

- cooling water flowrate

- cooling water temperature

In addition to this PLC, operation of the entire ozone plant is controlled either automatically or manually via main programmable process controller of type such as SIEMNS SIMATIC S7-300 or similar, which operates as MASTER for all ozonation process steps.

MASTER PLC system is installed in ozone generator room (or in central control room) as a remote controller of the entire ozonation process. It can be incorporated in operation and control system of the entire plant when such system is installed in the plant.

Charts of all characteristic parameters can be seen on integrated high-resolution display as information on errors in the system operation. All information shall be protected by security codes.

The following parameters and equipment are automatically monitored on Master PLC:

- operation of ozone generator

- operation of ozone destruction unit including fan

- operation of ozone concentration measuring equipment (for total ozone production)

- system for ozone introduction into water (distribution of ozone gas into each contact chamber)

- ozone production capacity depending on ozone dosage and water flowrate.

System automatically stops or gets in stand-by mode in case of any serious failure or equipment damage.

3.3.5 Ozone introduction into water

Ozone produced in ozone generator is introduced into chambers for water ozonation (ozone introduction) through independent stainless steel piping system.

As already said two independent lines for ozone introduction into water have been designed. This has been done for higher reliability of the system operation. In case that one ozonation line fails, which happens rarely but still it may happen (e.g. due to diffuser breakdown), this line is switched off until failure is removed, and in the meantime the second line having optimal capacity of 500 l/s may be loaded with 1000 l/s so that supplying the consumers will not be substantially threatened even if the breakdown occurs during peak consumption.

Chromium steel piping DN 32 with pressure of 5-6 bar has been adopted for oxygen transport from gas station to ozone generator. From ozone generator to diffuser system ozone is fed by stainless steel piping DN 32. All gaskets and seals in transport system are of Teflon.

For ozone introduction into water in chambers, ceramic diffusers are used which form fine ozone gas bubbles and inject them into main water flow.

On the bottom of the first chamber in each of two lines for ozone introduction into water, a distribution lateral system with pipes of stainless steel DN 32 which cover the entire chamber surfaces is installed so that 6 laterals are installed. On laterals T-branches DN 32 are mounted onto which ozone diffusers are screwed. Laterals rest on three concrete posts of dimensions 15x15 cm.

Each of two water ozonation lines is independent and through valve system can be switched on or off from ozonation function. Valves are installed on supply pipings DN 32 in room where ozone generators are installed.

The first chamber of each line serves for introduction of high ozone concentration near the bottom to enable as long contact of ozone bubbles with water as possible. The second chamber serves to achieve required contact time for ozone reaction in water. In order to carry out successfully these processes, water depth in chambers should be around 5 meters, and in this case is 4.85 m.

All parts in contact with ozone shall be of stainless steel or special materials highly resistant to corrosion. Of such construction can also be gas diffusers whose casing with bearing structure is of stainless steel and diffuser of ceramic with the following operating characteristics and dimensions:

- type				cylindrical ceramic diffuser

- dimensions			 	178 mm

- gas flowrate:

- nominal				2.2 Nm3/h

- maximum				3.0 Nm3/h

- minimum				0,3 Nm3/h

- materials:

- porous diffuser			ceramic

- diffuser support			316 L

- mounting hole (screwing)		316 L

- number of pieces 2x33                  	66

3.3.6 Ozone destruction system (Ozone destructors)

Catalytic destructor being cheaper and easier for handling has been selected.

Undissolved ozonated gas is absorbed from space above ozonation chambers and fed for destruction to catalytic destructor. Ozone concentration in gas released into atmosphere shall not exceed 0.1 ppm. Air stream absorbed from reaction chambers enters into ozone destructor via fan to preheating zone where off-gas is reheated to temperature 15-20C above inlet temperature. With such temperature gas stream is directed toward catalytic reactor zone, where ozone is catalytically destroyed. Condensate generated on this occasion accumulates on the destructor bottom and can be returned to ozonation chambers or released into sewerage.

In order to avoid underpressure, ozonation chambers shall be aerated and for this purpose aeration pipe DN 150 installed on the roof in chamber corner for ozone introduction has been foreseen. The pipe shall protrude 0.5 m above the roof. In order to enable air circulation, two openings DN 100 have been foreseen in each partition wall between two chambers.

Destructor technical characteristics are:

- number of units			one operating+one standby

- type					catalytic with preheating COD

- pre-heating				electric

- gas flowrate				up to 43 Nm3/h

- inlet temperature			20C

- control					relay

- installed power			0.27 KW

- fan installed power			0.65 KW

- dimensions

- length x width x height		 1000 x 600 x 1600 mm

- weight				 300 kg

3.3.7 Required quality of fluids used

In order to have normal, quality and long-lasting system functioning, inlet fluids: oxygen and water shall be of appropriate quality. Parameters to be satisfied by these fluids are, as follows:

- Inlet gas (oxygen) quality

- required oxygen quantity to produce

6.5 kgO3/h with concentration 10%		43.5 Nm3/h

- operating pressure				1.1 bar

- oxygen concentration in inlet gas		99.7-99.9%

- liquid oxygen pressure			5-7 bar

- dew point					 -70C

- hydrocarbon content				 20 ppm

- inlet temperature				 5-30C

- Cooling water quality

- inlet temperature	 			2-25C

- water volume (flowrate)			16 m3/h

- temperature increase				3-5 K

- normal operating pressure			 1-2 bar

- pH						6-8

- suspended matters				 1 mg/l

- iron						 0.3 mg/l

- manganese					 0.05 mg/l

- chlorides					 100 mg/l

- hardness					 8DH

- conductivity					 600 S/cm

- Ambient air (because of el. parts)

- temperature					 35C

- humidity (condensation free)			 70%

3.3.8 Ozone generator cooling

Cooling of new ozone generators has been foreseen as well as cooling of the existing ozone generators from clear water tank located above the plant. Water volume required for cooling the ozone generator shall be 5 – 10 m3/h and such water volume can be provided from the tank located above the plant in which water is pumped from the plant clear water tank by domestic waterworks pumps.

For cooling the existing ozone generators from tanks above the plant to ozone generator mechanical room a pipework DN 80 has been installed which will be used for cooling the new ozone generators.

## 3.3.9 Liquid oxygen gasification station

## 3.3.9.1 Technical description

Liquid oxygen gasification station is to be located in open space, alongside internal road, opposite to headquarters and mechanical workshop.  When selecting location of the liquid oxygen station it has been taken into account that all other facilities are at prescribed distance from the station.

Storage tank is mounted on own concrete foundation, and other equipment is installed on the station plateau.

Facility dimensions of liquid oxygen gasification station are 6.0 x 5.5 m. Gasification station plateau is elevated 20 cm from surrounding terrain, except on the side towards approach road. The station is enclosed with metal wire fence 2.5 m high with two gates. Two gates 2.0 m wide have been foreseen in the fence toward approach road. On the opposite side, one gate 1.0 m wide has been foreseen in the fence for emergency case. In addition to technological equipment, fire equipment, signboards and traffic signs have been foreseen, all according to appropriate Regulation.

Tank is mounted onto own foundation, and atmospheric evaporator is mounted onto steel section support that is fixed to gasification station (GS) concrete base.

The foundation of liquid oxygen gasification station and point of transfer are built with concrete. The said areas shall not contain matters of organic origin (oils, grease, etc.), as well as fuel matters.

Liquid oxygen gasification station comprises of the following:

- Storage tank of 20 m3 capacity, maximum operating pressure 16-18 bar.m.

- Atmospheric liquid oxygen evaporator of 100 m3N/h maximum capacity

- Pressure reducing station for reducing pressure to required operating pressure in main piping, complete with shut-off, measuring, control and safety valves and fittings

- Connecting pipings and valves and fittings.

Location of the gasification station has been selected taking into account allowed distances from other significant facilities, available space, approach roads and vicinity of facilities in which oxygen is used, all in accordance with the valid regulations for installing fixed vessels for liquid atmospheric gases (The Official Gazette of SFRY, No. 39/88).

Storage tank is equipped with necessary valves and fittings for correct and functional operation, including necessary shut-off, measuring, control and safety valves and fittings.

Filling of storage tank with liquid oxygen is carried out from special tank vehicle which is equipped with transfer pump, special flexible transfer hose (component of tank vehicle). Approach plateau in protective transfer zone shall be of concrete.

Gas distributer shall be responsible for filling the tanks.

For tank vehicle approach to the station and its installation at point of transfer for supplying the tanks with liquid oxygen, the existing road is used which is reconstructed and constructed using non-combustible material - concrete in the part of station in protective zones.

No grass, weed and other plants, as well as other organic material (asphalt, oil, grease, etc.) shall be at the distance of minimum 5 m from liquid oxygen tanks. If there are sewer gully traps in this zone, they shall be relocated.

For this reason a part of road in this zone and across the whole station width shall be built with non-combustible material (concrete). Space between contact edges of concrete slabs shall not be grouted with bitumen or other combustible material.

At the distance of 5 m from liquid oxygen vessel and on the point of transfer zone (7.5 m filling connection) smoking and naked flames are forbidden.

### 3.3.9.2 Basic characteristics of TO2 gasification station installation

- Vessel operating pressure:			             max. 18 bar

- Operating pressure in consumption piping:	             4 – 6 bar

- Installation operating capacity:				40 mN3/h oxygen.

### 3.3.9.3 Description of technological process in liquid oxygen gasification station

Technological process, according to which the station operates, is characterized with the following phases:

- transfer of liquid oxygen from tank vehicle to storage tank,

- storing of liquid oxygen in storage tank,

- taking liquid oxygen out of tank and transport toward evaporator,

- gasification, i.e. conversion of liquid into gaseous oxygen in atmospheric evaporator,

- reduction of pressure to required operating pressure in piping distribution network,

- transport of gaseous oxygen by main piping at required operating pressure.

### 3.3.9.4 Basic components of GSTO2

- Vertical, fixed vacuum insulated tank for the storing of liquid oxygen of 20 m3 capacity, with all necessary shut-off, safety, control and regulation valves and fittings.

- Atmospheric evaporator of 100 m3N/h nominal capacity.

- Reduction station for pressure reduction of gaseous O2 to the required operating pressure in main piping with of 100 m3N/h capacity; it consists of two parallel lines with regulating, measuring, shut-off and safety valves and fittings.

- Shut-off, safety, measuring-control equipment and pipings. Pipings in GSTO2 shall be made of Č.4580 austenic stainless steel pipes, shape and dimension according to JUS C.B5.221 Standard.

- Firefighting equipment and warning boards.

All equipment of gasification station is mounted on foundation in open space. Facility GSTO2 is enclosed with metal wire fence.

### 3.3.9.5 Storing of liquid oxygen

Storing of oxygen is carried out in fixed tank with capacity of 20000 l of liquid oxygen. The tank is fixed vertical pressure vessel with double wall and vacuum perlite insulation. The inner vessel serves for storing of liquid oxygen and is made of material suitable for operation at low temperatures (austenic chromium nickel steel). Gap is filled with non-combustible insulation powder (perlite) under high vacuum.

The tank is equipped with all necessary shut-off, safety and measuring-control equipment and valves and fittings, which are installed in control cabinet on front side of the tank.

Content of the tank is controlled by differential pressure gage and the pressure in the tank by pressure gage. Automatic pressure control is carried out by regulation / economizer valve.

From the tank liquid streams toward main atmospheric evaporators in which liquid evaporates and so evaporated gas streams toward reduction station at pressure to which the regulator through piping of gas phase is adjusted.

On the piping connected with the tank vapour space safety valves are installed to protect the tank from pressure rise. Overflow valve is used to control the tank fill. To secure outer vessel a safety membrane is used.

### 3.3.9.6 Gasification of liquid oxygen

Gasification of liquid oxygen is carried out in atmospheric evaporator, i.e. conversion of liquid oxygen in gaseous state of aggregation. One atmospheric evaporator in GSTO2 has been foreseen.

Liquid gas is fed for consumption from the tank by piping connected to the tank connection at pressure to which the tank is adjusted. Consumption piping is made of degreased Č.4580 austenic stainless steel pipes.

Technical characteristics of atmospheric evaporator are, as follows:

- Nominal capacity:                                            100 Nm3/h oxygen

- Maximum operating pressure:                        25 bar

- Test pressure:                                                  40 bar

Atmospheric evaporators are installed on own support of steel sections. The support is fixed to GSTO2 concrete foundation.

Gaseous oxygen is fed from evaporator to reduction station by gaseous phase piping.

### 3.3.9.7 Reduction station

Reduction station is intended to reduce piping pressure to required operating for consumption. It comprises of two parallel lines of which one is in operation and the other is standby. A bypass with globe valve around both reducing valves has also been foreseen. On each the following valves and fittings are installed:

- reducing valve for oxygen p1/p2= 13 /6 bar.

- globe valves before and after reducing valve and bypass

- filter before reducing valve

- safety valve after opening pressure reducing valve,

- pressure gages on reducing valve inlet and outlet

A safety valve potv=25 bar.m is installed on the piping after evaporator to protect the piping between two shut-off valves from bursting at work interruption.

Main piping of Č.4580, dimensions 33.7x2 mm, by which oxygen at required pressure is fed toward consumer, is connected to outlet connection of the reduction group.

## 3.3.9.8 Gaseous oxygen main piping

Main gaseous oxygen pipings are made of seamless Č.4580 stainless steel. Main oxygen piping of dimensions Ø33,7 x2 mm runs from reduction station outlet connection of gasification station to the facility with ozone generator.

From the station to the ozone generator facility the main piping runs underground in trench at the depth of minimum 800 mm from the piping top generating line. After emerging from ground, immediately next to ozone generator facility, the main piping runs on the facility façade at minimum height of 2,5 m and enters the facility in the vicinity of ozone generator. Upon entering the facility, the piping runs on the wall to location in front of the ozone generator. A three-way globe valve DN25 NP25 of stainless steel is installed on the end of the piping.

3.3.10 Valves and fittings

3.3.10.1 Sluice gate

At water inlet to the ozonation chambers installation of sluice gate whose guides are “adhered-screwed” on wall, of the following characteristics:

- Width: 							1000 mm

- Height: 						1000 mm

Application of this type of the sluice gate shall require extension of the existing circular opening of 600 mm diameter to opening of 1000x1000 mm. Easy and fast assembly to place foreseen is possible.

Replacement of the existing sluice gate on ozonated water outlet in concrete channel of the following characteristics has been foreseen:

- Width: 							1400 mm

- Height: 						2000 mm

Material:

- Guides: stainless steel

- Sealing: polyethylene UHMWPE or similar.

- Sluice gate body: stainless steel

- Shaft: stainless steel

Construction of the sluice provides two-way (upstream-downstream) leakproof on all four gaskets (lateral, bottom and top).

The opening of the sluice gate is carried out by rotating the shaft. Shaft thread is such that it cannot be immersed in liquid penetrating into chamber.

Electric actuator has been foreseen for opening and closing the sluice gate. Speed of the sluice gate opening-closing should be lower or equal to 0.05m/s. Maximum power of the actuator should be 3 kW. The opening of the sluice gate can be also carried out manually by turning appropriate crank. Electric actuator has been foreseen for external installation – resistant to immersing IP68.

3.3.10.2  Valves (with short body)

Installation of gate valves has been foreseen on the piping for outlet and discharge of the ozonation chambers. Valve is used as a shut-off organ at discharging ozonation chambers. In regular operation valve is always closed.

Assembly dimensions of the valves are in accordance with JUS (DIN) Standards: JUS M.C5.005 (DIN 3202). Flange connecting dimensions are in accordance with   JUS M.B6.011 (DIN 2503) Standard.

Gate valves have been foreseen on piping DN 150 for outlet and drainage of ozonation chambers and to be made of stainless steel so as to be resistant to aggressive effect of ozone.

Valve shall be with flanges and rigid valve wedge. Valve activation is manually, by wheel, by turning axial stationary shaft.

3.4.	Filtration

Following ozonation, water is conveyed to gravity filters.  There are a total of 8 filter fields (surface area 12.6 x 5 meters).

Existing filters are gravity-type sand filters.  The water enters at a single central location and thus disturbs the surface of the filter filling, particularly after cleaning.

Based on the problems currently experienced with the existing sand filters, the design calls for  reconstruction as follows:

- Replacement of the filter filling with a sand/anthracite filling;

- Installation of overflow channels for the delivery of water to the filters; and

- Reconstruction of the pipe gallery.

The basic undertaking aimed at improving the water quality following filtration is the replacement of single-layer filters with dual-layer filters of quartz sand and anthracite. The ozone content of the water delivered from the ozonation station should not exceed 0.4 mg/l.

The design calls for the replacement of filter nozzles on the concrete slabs of the dual-bottom filters. Prior to this activity, the condition of the concrete slabs and their horizontality and stiffness should be tested and, based on the test results, appropriate measures should be taken to ensure the required level of quality and accuracy.

The design also calls for the reconstruction of the raw water supply line to the filters; a channel should be installed along the filter field such that the water is delivered to the filters via the channel along the entire length of the filter, so as not to disturb the filter filling. This will also allow for a uniform flow of water to each of the 8 filter fields and ensure uniform operation and loading of all filter fields.

Existing valves on the water supply line to the filters will be replaced with obturators – pneumatic valves installed in the channel wall. The bellows of the valve will inflate and shut off the flow of water to the filter while it is being cleaned.

Main design characteristics of the filter units:

- Flow rate: 			950 l/s or 3,420 m3/h

- Field size: 			12.65 m

- Number of fields:		8

- Surface area: 			63 m2 (504 m2)

- Filling height:

Gravel	 	                   	0.1 m

Sand 	 		             0.8 m

Anthracite 	 	             0.3 m

Top layer of water:   	             0.8 m

- Filtration rate:

All in service: 			6.8 m/h

One being cleaned:		7.6 m/h

- Filling:

Quartz sand: 	                         Cunif  1.4       dav  1-1.2 mm

Anthracite, hydrocite type:      dav  1.4-2.6 mm

- Filter cleaning:                     	air + water

Filter operation will be controlled either from the WTP’s CC or via control panels.  Existing control panels are to be replaced with up-to-date units.

In addition to automated operation of the filters, it should also be possible to manually clean the filters, with direct operator insight into the cleaning method and effectiveness for each individual filter.

The air in the filter area should be ventilated and the filter fields protected from direct sunlight.

Filters will be cleaned as follows:

- loosen material with air (about 10 s)

- clean with water and air (5 min)

- flush with water (10 min)

To ensure appropriate cleaning of the filters, it will be necessary to provide a cleaning rate of 26 m/h, which requires 456 l/s of filter cleaning water.  Water-and-air cleaning requires a water flow rate of 13 m/h, or 228 l/s.

The air flow rate required to loosen the filter filling is 50 m/h, such that an air supply of 52.3 m3/min should be provided.

3.5.	Pipe gallery

The filter-cleaning water supply pipe must be replaced because the diameter of the existing pipe is DN 400, while the required diameter of this pipe is DN 600. The required flow rate of the filter cleaning water is 456 l/s, such that the flow velocity in the DN 600 pipe has to be 1.6 m/s.

The following pipes will also have to be replaced:

- air supply pipe for filter cleaning, DN 200

- clean-water discharge pipe, DN 250

The existing valves on the pipes will have to be replaced with pneumatically-driven valves and a new manually-driven gate valve added so that the entire facility will not have to be shut down if a pneumatic valve fails.

The work on the pipe gallery should be carried out in stages, filter by filter, so as not to interfere with the operation of the plant.  Wherever this is not possible, all preparations should be made properly to minimize the plant's downtime.

3.5.1 Delivery of water to sand filters

Following ozonation, water will be conveyed to the sand filters by means of a 1.4 m-wide concrete channel which runs along the entire length of the filter gallery. The water will enter the overflow channels via 80 x 40 cm openings equipped with new valves (obturators).  Following reconstruction of the raw water supply line to the filters, involving the installation of an overflow channel along the filter field, water will be delivered along the length of the filter, will not disturb the filter filling, and will ensure uniform operation and loading of all filter fields. The overflow channels will be made from 3 mm-thick stainless steel to facilitate installation. The length of the overflow channel will be 5 m.  Four stainless-steel supports, spaced 1 m apart, will be installed to reinforce the overflow channel.

Existing valves on the water supply line to the filters will be replaced with obturators – pneumatic valves installed in the channel wall. The valves will be used to shut off the flow of water to a filter while it is being cleaned. Their bellows will be inflated to accomplish the shutting off. The obturators will be made from special rubber resistant to the ozone present in the water.  The rubber bellows will be inserted in a metal frame attached to the channel wall and thus the obturator installed on the filter.  This valve will be connected to an electro-pneumatic control valve located in the control cabinet of the pipe gallery.

3.5.2 Discharge of filtered water from the sand filters

A DN 600 pipe which carries away clean water and delivers filter cleaning water will be connected to the lower portion of a V channel.  A DN 250 clean-water discharge pipe will be connected to the DN 600 pipe by means of a T piece.  The existing DN 250 pipe will be replaced.

There will be an automatic DN 250 pneumatically-driven butterfly valve on the DN 250 pipe. The automatic butterfly valve is a regulating valve which will control the operation of the filter, that is, it will maintain a constant water level in the filter field regardless of its current level of cleanliness (or its current throughput capacity) and the amount of water delivered to the filter.  This valve must be fully closed while the filter is being cleaned. The pneumatically-driven control valve will have current position indicators and signaling of open/closed positions. A dismantling piece will facilitate installation and removal of the valve, if necessary.

A DN 250 electromagnetic flow meter will be installed on the clean-water discharge pipe from the filter.  It will be used to monitor the operation of the filter and the amount of water which passes through the filter.  It will provide additional control of the amount of water delivered to the filter.

3.5.3 Water supply for cleaning sand filters

The main pipe which will deliver filter cleaning water is DN 600, installed along the pipe gallery. It will replace the current DN 400 pipe.  Special DN 600 branches will run from this pipe to each filter field.  They will be connected to the bottom section of the V channel.

There will be an automatic pneumatically-driven DN 600 butterfly valve on each branch. This valve will be open while the filter is being cleaned and fully closed while the filter is in service.  This is not a regulating valve, but an on/off valve.  There will also be a dismantling piece on the pipe to facilitate installation and removal of the valve, if necessary.

3.5.4 Discharge of sand filter cleaning water

While the filters are being cleaned, the water will pass through the filter filling from the downside up.  Following passage through the fluidized filter filling, the water will overflow into oval canals which will deliver water to the bottom section of the V channel.  Water is directly routed from the channel to outlets which end with view covers in the channel that delivers the cleaning water to the sedimentation basin. The design does not call for the replacement of view covers on the water discharge line.

3.5.5 Air supply for cleaning sand filters

The trunk line in the pipe gallery will be DN 200 and separate branches will run vertically downward to each filter field.  The existing pipe on the pipe gallery will be replaced with a new DN 200 pipe.  There will be an automatic DN 200 pneumatically-driven butterfly valve on the vertical section of each branch. The valve will be open while the filter is being cleaned and closed while the filter is in service.  This is not a regulating valve, but an on/off valve.  It will signal open/closed positions. There will also be a dismantling piece on the pipe to facilitate installation and removal of the valve, if necessary.

3.5.6 First filtrate

A DN 200 first-filtrate discharge pipe will be connected to the dual-bottom of the filter and its function will be to fully discharge the dual bottom.  The DN 200 pipe is connected to a DN 200 pipe via a T piece.  The existing pipe will be replaced with a new DN 200 pipe.

There will be a DN 200 pneumatically-driven butterfly valve on the DN 200 pipe. This is an automatic on/off butterfly valve, which will always be closed when the filter is in service and open only when the dual bottom of the filter needs to be fully discharged.  A dismantling piece will facilitate installation and removal of the valve, if necessary.

3.5.7 Inspection manholes

Each filter field will have an inspection manhole to the dual bottom. This manhole will be an embedded DN 600 pipe with an anchor flange. On the side of the pipe gallery, the pipe will be provided with a flange to which a bland flange will be bolted. The blind flange closes the inspection manhole.  The existing inspection manholes are corroded and will be replaced with new manholes.

3.6.	Filter - cleaning pumping station

Pumps and compressors for water and air cleaning of the filters will be located in the WTP's engineering room.

There are three low-pressure compressors in the pumping station for air cleaning of the filters. They were manufactured by FAGRAM and their characteristics are:

- Q = 25.8 m3/min

- p = 0.5 bar

- P = 37 kW

The required filter-cleaning air flow is 52.3 m3/min, so that the existing compressors can provide sufficient filter-cleaning air.  The discharge pipe of the compressor will have a relief valve which will be used to control the flow rate of filter-cleaning air.  This will be a pneumatically-driven butterfly valve with EP regulation.

The design calls for the installation of two new centrifugal pumps of the following characteristics:

- Q = 228 l/s

- H = 8.7 m

- P = 30 kW

These will be single-stage centrifugal pumps in spiral casings according to ISO 2858. The suction connection is horizontal, while the discharge connection is vertical, facing upward. The thrust will be balanced hydraulically, by means of back paddles.  The shaft will be sealed by means of twisted gaskets or a mechanical seal.  Ball roller bearings will be provided.  Bearings will be lubricated with oil and an automatic device provided to dispense and maintain oil level. A flexible coupling will connect the drive motor to the pump.

Pump flow will be regulated by means of a frequency controller, where the RPM will be set to control the pump depending on the required flow rate for filter cleaning purposes.

The pumps currently draw water from a tank which contains clean but not chlorinated water. The suction pipe is currently DN 400 and needs to be replaced with a larger diameter pipe, DN 600.

The following will be provided on the suction line of each pump:

·	manually-driven butterfly valve DN 400 NP 10

·	dismantling flange DN 400 NP 10

The following will be provided on the discharge line of each pump:

·	return valve DN 400 NP 10

·	manually-driven butterfly valve DN 400 NP10

The collector pipe of the pumps will be DN 600, on which an electromagnetic flow meter and a sectional valve, DN 600, will be installed. Flow meter signals will be routed to the CC.

It will be possible to control electrically-driven butterfly valves and pump start remotely from the CC or manually on the spot.

3.7. Disinfection of water with sodium hypochlorite solution

Water will be disinfected with a sodium hypochlorite solution obtained from the electrolytic chlorine production unit, in the form of a sodium hypochlorite solution at the point of consumption, in a safe manner, since no gaseous chlorine is created during operation.

The procedure is as follows:  Piped water is conveyed to a softener where calcium and magnesium ions are stripped to soften the water.  The softened water is conveyed to the electrolyzer by means of a dispensing pump, where it is mixed with a sodium chlorite solution which is delivered by another dispensing pump from a tank which holds a concentrated solution of sodium chlorite. A chemical reaction takes place in the electrolyzer (DC power supply), where the solution is converted into hypochlorite and discharged into a tank.  Hydrogen is generated during the hypochlorite synthesis reaction, which is ventilated into the atmosphere.  The obtained hypochlorite solution is injected into the pipeline by means of diaphragm pumps. The analyzer receives chlorine concentration information and maintains the set concentration by means of the pumps. This method ensures continuous hypochlorite production and automated control of the process, dispensing and residual chlorine measurement.

The maximum flow rate of the Majdevo WTP is 1000 l/s, while the maximum chlorine dose can be as high as 1.0 mg/l. Consequently, 3.6 kg/h of chlorine is required to disinfect treated water.

The basic characteristics of the system which will produce sodium hypochlorite from salt on the spot and dispense the solution are:

- Number of units: 			4

- Total equivalent chlorine capacity: 	(Cl2) 4.0kg/h

- Flow rate of saturated solution: 		30% 40l/h

- Flow rate of softened water: 		360l/h

- Total electrolyte flow rate: 		400l/h

- Salt consumption: 			~ 12kg/h

- Electric power consumption: 		~ 20kWh

- Supply voltage: 			150-270V, 50Hz

- Output concentration NaOCl 		0.9-1.0%

- Size of station (W x D x H) 		2500 x 2750 x 2800 mm

3.8. UV disinfection

Instead of chlorination, UV light is used to destroy in one second all the microorganisms that may be present.  The most efficient range is the germicidal range of UV radiation - 200 - 300 nm.

The UV radiation unit will be installed on the DN 1000 gravity pipeline which will deliver water to Kruševac. The water will be chlorinated only with a low concentration of chlorine to provide the necessary residual in the network.

Two UV disinfection units have been selected (2120 m3/h each), plus one standby unit with the same capacity. The size of the UV disinfection unit is 1060 x 2400 x 1380 mm, and its power consumption is 11.6 kW.

A DN 700 electrically-driven butterfly valve will be installed before and after each UV disinfection unit.  These valves will facilitate replacement of the operating UV disinfection unit or removal for overhaul, as necessary.

3.9. Sedimentation basin/lagoon

The sedimentation basin/lagoon will be a structure located in the area of the existing earth lagoons under the main road from Kruševac to Brus. It will have to receive large amounts of water from the filter cleaning operation, which are generated over a short period of time, and all other water generated during the water treatment process.

This structure has been designed as an open lagoon comprised of an inflow manhole, two retention chambers, and an outlet channel.  The volume of each retention chamber has been selected such that it can accommodate the entire amount of water from cleaning of a single filter.

The inflow manhole will be equipped with a DN 600 valve (manually-driven gate valve), which allows for one chamber to be shut off when it needs to be discharged and the sludge cleaned.

The chambers will discharge into the outlet channel via a flexible-hose floating overflow. The discharge/drainage will last for about 5 hours, thus providing sufficient residence time and allowing for the sludge to settle.  The outlet channel will be emptied via a DN 600 pipe which will convey the water to a channel by means of gravity.

Periodic cleaning of the chambers, as required, will be accomplished by disconnecting the respective chamber by means of valves, pumping out the sludge and transporting the sludge by means of a special vehicle to a landfill or designated location.

The lagoon itself is a reinforced-concrete structure, 26 x 15 m. The useful volume of each chamber is 23 x 7 x 2.5 = 400 m3, which is more than enough to accommodate filter-cleaning water and allow for a residence time of 5 hours before the next filter is cleaned.

4. VALVES AND FITTINGS

4.1. Pneumatically - driven butterfly valves

The pipes on the pipe gallery, which supply filter-cleaning water, supply filter-cleaning air and discharge filtered water, will be outfitted with pneumatically-driven butterfly valves. These butterfly valves will be used to control the operation of the facility.

The installation sizes of the butterfly valves will company with JUS (DIN) standards: JUS M.C5.005 (DIN 3202). Butterfly valve flanges will comply with the JUS M.B6.011 (DIN 2503) standard.

All valves in the pump-and-compressor station will be made from the following materials:

- Housing		SL 25 (grey iron)

- Disc		GGG-40/Ni (nickel-plated grey iron)

- Shaft		stainless steel Č 4171

- Rubber packing 	EPDM

- Sleeve 		Acetal

- Gasket 		EPDM

Valves will be opened and closed remotely from the CC or locally, at the pumping station, by means of a pushbutton.

4.2. Gate valves (short-body)

Short-body gate valves will be installed at the suction and discharge ends of the cleaning water pumps. Short-body gate valves will also be installed on the supply line leading to the sedimentation tank.

Each gate valve will be used as a shut-off component while the pumps are being serviced.  The gate valve is normally open.  It is closed only during overhaul or valve maintenance activities.

Installation sizes of the gate valves will comply with JUS  (DIN) standards: JUS M.C5.005 (DIN 3202).  Installation flange sizes will comply with the JUS M.B6.011 (DIN 2503) standard.

The gate valve will be comprised of flanges and a stiff wedge. The gate valve is operated manually, by means of a turnwheel which moves a stationary axial shaft.  The gate valve housing, disk, and turnwheel will be made from grey iron.  Sealing rings and shaft nuts will be made from bronze.

4.3. Dismantling pieces

Dismantling pieces will be used as connection elements because they facilitate installation of valves and pipe fittings and allow for adjustment of the installation length to within +/- l.

The rated pressure of the flanges on dismantling pieces will be PN 10. Installation flange sizes will comply with the JUS M.B6.011 (DIN 2503) standard.

The dismantling flange will be comprised of a flange, inserted flange and tightening piece.  Sealing will be achieved by tightening the sealing element, O-ring by means of the tightening piece.

The flange, inserted flange and tightening piece will be made from high-quality steel castings.

4.4. Check valves

The DN 400 discharge pipe of the pumps will have a butterfly check valve, including a counterweight DN 400 PN 10 with flanges.  Check valves will be used to prevent return flow of the fluid.

The rated pressure of the check valve flanges will be PN 10. Installation flange sizes will comply with the JUS M.B6.011 (DIN 2503) standard.

The check valves will be made with a double eccentric body and rotated by means of a shaft which has a lever and counterweight at its left end, viewed in the direction of the flow.  The role of the counterweight is to move the shut-off body before the fluid velocity equals zero, and thus reduce the amount of the fluid which will return through the check valve and decrease the inertia.

The housing and shut-off body will be made from grey iron, while the shaft will be made from corrosion-proof steel.  Sealing elements will be made from EPDM.

4.5. Flow meter

Measurements by means of an electromagnetic flow meter are based on Faraday’s law of electromagnetic induction. The EM flow meter is comprised of two main components:  sensor for the creation of a magnetic field in the pipe, and an electronic power supply, gain and signal processing assembly.

Technical characteristics:

- Measurement range 0-60 l/s

- Sensitivity threshold 0.1-1.0 mm/s

- Test pressure 1.5 * NP

- Working temperature Tmin = -20 C, Tmax = 60 C

- Internal overlay of the sensor:  as recommended by the manufacturer depending on the chemical composition of water

- Protection: IP 67 (IEC 529 or DIN 40050)

- Output signal: current 4-20 mA and pulse

- Measurement accuracy (v  0.5 m/s, error +/- 0.5% of the flow rate)

- Submersion:  the sensor must be completely filled with water at all times (as shown in the figure)

4.6. Control (0-6 bar) pressure gage with three-way valve

A pressure gage whose measurement range is from 0 to 10 bars will be installed on the discharge pipe of the pumps (upstream and downstream from the gate valve).  A 0-2.5 bar pressure gage will be installed on the discharge connections of each low-pressure compressor.

A G ¾” three-way valve will be used to connect the pressure gage with the respective pipe.

The three-way valve is normally closed. It is opened only when the pressure in the supply pipe needs to be checked.

4.7.  Pipes and molded pieces

The existing pipes on the pipe gallery for the supply of cleaning water, the supply of cleaning air, the discharge of clean water, and the discharge of the first filtrate will be replaced.

The pipes on the pipe gallery must be made from stainless steel or must be steel pipes with anti-corrosion protection.  The main advantage of stainless steel pipes over steel pipes is the absence of corrosion.  As such, they are not susceptible to damage but the cost of stainless steel pipes is higher than that of steel pipes.

Č.0361 steel will be used to fabricate the steel pipes. These pipes will be welded longitudinally or spirally.  Steel pipes to be installed as part of this project will comply with the EN 1092-1 standard.

Stainless steel pipes will comply with ISO/metric sizes and the  EN 10217 or EN 10216 standard, and tolerance will be per the EN ISO 1127 standard.

Pipes will be connected by welding on the spot, including the required valves via flange connections.

All pipes will be appropriately supported to prevent any distortion of the equipment. Pipes on the pipe gallery will be suitably anchored and supported on the floor.

The overflow channel of the sand filters will be made from stainless steel sheeting of standard format and surface. The quality will be per 1.4301 (Č.4580).

Stainless steel sheeting will be delivered in accordance with the European standard EN 10088.

5.	CONTROLS AND ELECTRICAL INSTALLATIONS

## 5.1.	Power supply for newly-designed consumers

Consumers included in this project will be supplied from the following newly-designed low-voltage primary and secondary distribution boards, 0.4kV:

- diesel-generating set main distribution board, +2NE,

- auxiliary power supply system, 24V DC, +1NU,

- pumping station main distribution board, +1NG (existing board replaced),

- ozone generator main distribution board, +2NG (existing board replaced),

- flocculation distribution board, +3NG,

- filter distribution board, +4NG,

- sluice gate board, +2NG.1,

- gasification station board, +2NG.2,

- general-purpose distribution board, +3NG.1, new flocculation station.

The newly-designed priority consumers will be supplied from the +2NE main distribution board located in the diesel power pack (DPP) room, adjacent to the existing distribution board =1U. The distribution board will be made from steel sheet and installed on the wall.

The capacity of the existing DPP is sufficient to supply both existing and new consumers.

The distribution board +1NU will be used for battery 24VDC power supply within the Majdevo WTP.  It will be located in the engineering room (pumping station). The distribution board will have a modular rectifier set (3 modules, 1.7kW each), sealed VRLA batteries and DC distribution equipment.

The design of hydro-mechanical equipment calls for the replacement of two filter cleaning pumps of the following characteristics:

- Q = 228 l/s

- H = 8.7 m

- P = 30 kW

These pumps will obtain their power supply via frequency controllers.  Additionally, one existing high-pressure compressor (Atlas Copco GA 30, P=30kW) will be moved from the ozonation station to the pumping station.  Also, worn equipment will be replaced and the treatment process upgraded and automated.  Consequently, the existing distribution board in the pumping station will be dismantled and a new main distribution board (+1NG) supplied and installed. The +1NG will be comprised of a network power supply section and an emergency generating set section.  The approximate size will be 2400x2000x600 mm (WxHxD).  It will be installed next to the +RO-CS(A) cabinet which will be retained.

The network power supply section of the +1NG will be supplied from the main LW distribution board located in the transformer station (=1NE+1NE2), via a newly-designed cable, type 2x(PP00 4x95mm2), 1kV, while the emergency section will be supplied via a newly-designed cable PP00 4x95mm2, 1kV.

The design calls for the motors of the other pumps in the engineering building to be started by means of soft started.  The existing supply cables will be retained.

The main distribution board +2NG will provide power supply to the two new ozone generators and other consumers in connection with the ozonation process. It will be located in the ozonation building.  The main distribution board will be free-standing, comprised of two fields. Its total size will be (2x600)x2000x600mm (WxHxD).

The total installed power of the new ozonation station is Pi=177.4kW, while the simultaneous electric power is Pj=160kW (Ij=272A).

The existing supply cable PP00 4x185mm2, 1kV, runs through virtually dry sand.  The current carrying capacity (for a type D electric distribution board is) is Icc cap =257A (JUS N.B2.752, Table 4).

The actual current carrying capacity of the cable, laid in earth (our case), is obtained when adjustment factors are introduced, and it amounts to:

Iz=kθ*kλ*kn*Icc cap=0.95*1.55*1*257=378A> Ij=272A.  As such, the existing supply cable can be retained for the +2NG.

The distribution board +2NG.1 will be installed on the outer wall of the ozonation station and will provide power supply for three sluice gates.

The main distribution board +3NG will be located in the flocculation facility, in a free-standing cell - size 600x2000x500mm (WxHxD). It will provide general-purpose power supply to +3NG.1, and power supply to the polyelectrolyte preparation and dispensing unit +3NG.2, flocculation agitators and the PLC for the clarifying process.

Power to the new flocculation unit will be supplied via a new cable PP00 4x25mm2, 1kV, partially installed in existing cable trays and partially in an earth trench.

The main distribution board +4NG will be installed on the wall of the filtration station.  It will provide 230V AC and +24V DC to all filter panels.

Local control cabinets (filter panels) will be used to provide power supply and control filter valves.  They will be located on the pipe gallery and marked +1WF to +8WF.

## 5.2.	Cable routing

Supply cables for internal and external connections will be installed in wall saddles, protected SAPA tubes, earth trenches, new and existing trays or cable ducts.

The cables have been selected based on load, installation conditions, and the permitted voltage drop.

0.4kV supply cable are type PP00 or PP00-Y 600/1000V, with a suitable cable core and cross-section.

External cable routes have been selected to minimize crossing with other external installations.  However, wherever there is crossing or parallel routing with other installations, the appropriate technical conditions should be fulfilled.

## 5.3	General-purpose installations

The new flocculation unit will have industrial 2x36W fluorescent lamps (protection level IP65).  They will be distributed in accordance with the drawings included in the graphic documentation.  They will be accessible for easy handling.

Above each entrance door of the building, on the outside, there will be wall-mounted lamps with metal-halogen bulbs (150W, 230V).

Lighting installations will be routed by means of PP00 and PP00-Y cables, 1.5 mm2, on wall saddles.

All general-purpose installations of the flocculation unit will be supplied from +3NG.1.

All consumers at the gasification station will be supplied from +2NG.2, equipped with three HRC fuses 63A and a three-phase outlet PROP-IV-63A made from insulated material.  The cabinet will be installed on a steel post of the fence.

## 5.4.	Earthing and lightning rod installations

5.4.1 New flocculation unit

The new flocculation unit will be earthed via a galvanized steel tape laid in the foundations (FeZn 25x4mm), which will be connected with the existing earthing at a suitable point.  All metal parts which are not normally energized, but might become energized due to failure (climbing irons, pipes, steel structures, distribution cabinets, etc.),  will be connected via an equipotential bonding earthing busbar (EBEB).

The lightning rod is conventional (Faraday cage), made from FeZn 25x4mm tape, running over the roof on appropriate supports.  It will be connected to the foundation earthing via six lightning down conductors. Metal parts of the roof cover will be equipotentially connected by means of washers or welding.

5.4.2 Liquid oxygen gasification station

The liquid O2 tank and all other metal components will be earthed by means of an Fe/Zn 25x4mm tape laid in the tank foundation and connected to the existing earthing of the surrounding structures.

The O2 tank is a set of metal elements which are used both as a lightning rod and a lightning down conductor. Test clamps for the tank will be located at a height of 0.5m from the ground level, on the tank support.  Earthing will be provided by a Fe/Zn25x4mm tape placed in the concrete foundation of the tank, which will be welded to the foundation reinforcement in several places.  The foundation reinforcement will also be welded with a 20 cm overlap.  Such earthing will be connected with the earthing of the surrounding structures and will form a single equipotential assemblage.

Metal doors of the tank fence and tank pipes will be bypassed by a copper flexible braid bond (Cu 16mm2).

## 5.5.	Monitoring and control system

The Majdevo WTP will be controlled by a combination of electrical and pneumatic devices.  Each filter field will have a dedicated control cabinet (+1WF...+8WF) with a PLC, electrical peripherals and a valve island, installed on the pipe gallery.  Local control of the filters will be provided via operator dialog terminals (ODTs). The ODTs will be installed in separate consoles near the filter basins and oriented in such a way that the operator can see the surface of the filters behind the terminals.

In addition to filter control cabinets, various parts of the treatment process will be automated via interface cabinets (=W03.0+1NW, =W11.0+2NW, =W01.0+3NW) with a PLC and touch panel (ODT) mounted on the cabinet door.

The selected concept allows for local control on instruction from the main plant operator.

A SCADA system will be used to visualize the entire WTP process.

The configuration of the monitoring and control system is shown in Drawing 0.5 (block diagram of monitoring and control).

Control levels

The monitoring and control system will consist of three hierarchical levels:

Level 1:		Control Center  (SCADA System)

Level 2:		Station (PLC, »Station controller«)

Level 3:		Operating device (motor, sensor, converter)

Level 1

PC platform, appropriate application software, SCADA environment.

The application software will be fully consistent with the software requirements which arise from the treatment process design, mechanical design, and electrical design of the monitoring and control system.

Level 2

PLC, appropriate number of input/output modules, and application software.

The application software will be developed in one of the IEC 61131 languages. There is local communication via ODTs at this level.

Level 3

Pertains to operating equipment and devices, such as motors, frequency controllers, soft starters, transmitters and/or electrical measuring transducers (signal conditioners).

Executive devices have two operating modes:  LOCal and AUTomatic (selected by means of a selector switch, LOC - 0 – AUT).

LOCal operation

Used solely to test motors.  If the motor is driven via a frequency controller, it is jogged at a pre-defined speed.  A direct-start motor will run at its idle speed.  All protection functions are required for this operating mode (e.g., dry run protection of pumps).

AUTomatic operation

This is the »natural« operating mode of the equipment.  It is ensured by appropriate controller application software. Parameters can also be adjusted and monitored via ODTs.

Status signals and alarms

Local ODT signaling is provided for each direct-start pump.  It includes:

- LOC mode

- AUT mode

- In service

- Failed

Both local control panel and ODT signaling will be available for motors started via frequency controllers or soft starters.  The ODT will show the complete status of the frequency controller, in the same way as the local panel of the frequency controller.

- LOC mode

- AUT mode

- In service

- Failed

The ODT will also display all non-electrical parameters included in the list of measurement points.

The synoptic display for monitoring and control purposes will be a wall screen-type display (composed of 4 LCD screens, 52", with loudspeakers), mounted on the CC wall by means of appropriate supports. A special video wall server with appropriate software, connected to the office LAN network, will be used to control the wall display.

The LCD synoptic display will be visible from a very sharp angle and will allow for the operation of the entire system be obvious at a glance.

## 5.6.	Measurements

The purpose of the measurement equipment is to allow for continuous monitoring of parameters at characteristic points of the process, to provide insight into the status of the system, and to perform protection/safety functions.

Measurement methods, equipment and technical concepts have been selected to fulfill the requirements of the treatment process and to ensure a high level of reliability and safety for the plant and its operators.  The instrumentation is of the electronic type.

All measurements at the plant level (continuous and discrete) are shown in Drawing 0.4. The treatment process schematic of the Majdevo WTP is shown in the graphical documentation of the design.

## 5.7.	Video surveillance of the treatment process

Video surveillance will be provided for instantaneous monitoring from the CC.  Since the existing video surveillance equipment is at the end of its life cycle, it will be replaced with a new, modern system.

The following facilities will be monitored:

- Filtration station

- Sedimentation tank

- Ozonation building

Each of these facilities is equipped with a sufficient number of cameras installed in special waterproof housings.

A video server (video encoder), located in the CC, will provide a communication link with the monitoring and control system.  The video surveillance system will be incorporated into the SCADA system by means of an active communication switch.

## 5.8.	Protection of motors

Direct-start motors will be protected from short circuits and overloads by means of motor protection circuit breakers.  Motors started via frequency controllers or soft starters will be safeguarded by internal protection such as:

- Short-circuit protection between phases and between phase and earth;

- Over-current protection and overload protection during starting;

- Motor overload protection;

- Thermal protection (thermal imaging);

- Overvoltage and undervoltage protection;

- Detection of power outage and loss of phase.

## 5.9.	Protection from dangerous touch voltage

Protection from dangerous touch voltage will be provided by means of automatic shutdown of the power supply via over-current devices (TN-C-S system per JUS N.B2. 741 / IEC 364-4-41).

6.       STRUCTURAL REHABILITATION OF THE ENTIRE WTP

  - Reconstruction

Since the WTP has been in service for 25 years, certain structural components are damaged due to non-uniform settling of the structure, atmospheric impacts, and the aggressive environment in which the structural components are located.  Some of the structural damage is clearly visible while other shortcomings have been uncovered.

The WTP is comprised of the following main structures:

1.Administration building

2.Pumping station

3.Filtration station

4.Sedimentation station/pulsators

5.Ozonation station

6.Chemicals station

    - Administration building

This building is comprised of the following:

- Entrance,

- Lobby,

- Stairs,

- Offices,

- Halls,

- Restrooms,

- Changing room with showers,

- Laboratory,

- Kitchenette,

- Dining room,

- Control Center.

The stairs at the entrance of the administration building are finished with terrazzo which is cracked and should be replaced with marble plates similar to those found in the lobby.

The condition of restrooms on all floors is poor and requires complete replacement of installations, sanitary ware, ceramic tiles and doors.  Since men’s restrooms are more difficult to maintain, it is desirable to add a urinal installation in the area where there is only a sink at present.

The shower stalls in the changing room are completely worn and are currently not in use.  The stalls, water heaters, shower heads and fixtures must be replaced in their entirety. The corroded changing room lockers and the wooden doors should also be replaced.

The plant laboratory in the administration building is equipped with basic laboratory instruments, devices and chemicals for physicochemical analyses of the quality of raw and treated water. Since a lot of the equipment is old, it should be replaced.

The entire kitchenette should be equipped with appropriate kitchen elements.

Other than paining of the ceiling and replacement of windows, the Control Center does not require any work.

In addition to the above, all internal wooden doors should be replaced, metal doors painted, the walls and ceilings of the entire building painted, and the windows replaced in all rooms in the same way as already started.

The condition of the facade of the administration building is good, except for the painted parapets which are chipped.  Old coats of paint should be removed carefully and the base prepared for re-painting.

6.1.2  Pumping station

The condition of the pumping station structure is satisfactory. Inside walls, windows and the fence should be painted.  Additionally, concrete pump platforms should be covered with ceramic tiles.

6.1.3 Sand filters

The filtration station is the third stage of the WTP's treatment line.  It is comprised of:

- a filter hall with 8 filter fields, and

- a pipe gallery.

The following work is required:

- painting of windows and doors,

- painting of metal fence,

- paining of RC beams,

- cleaning of window panes from remains of paint and placing of foil on the glass.

At the filtration station, considerable damage of the concrete roof beams has been noted. In some places the top layer of concrete is missing and the reinforcement is visible and partly corroded.

The channels which run along the outer side of the structures and which connect the filtration, pulsator and ozonation stations have sustained the most apparent damage.  Water from the inside of the channel has been seen to seep onto external surfaces, suggestive of damage deep within the concrete (along the entire concrete section).  Icicles have been forming at these places during low-temperature periods. The largest icicles were seen at the intersection between the ozonation and filtration channels.

The top layers of the bottom of the channel and the columns are partially damaged and the reinforcement is visible.  This damage could be the result of atmospheric impact, inadequate design thickness, or improper workmanship.

Considerable damage, in the form of cracks and fractures, has been noted at working joints. The structural damage in these areas suggests that the joint behaves like an expansion joint and it should, therefore, be rehabilitated as such.

6.1.4  Pulsators

Corrosion has been noted on all metal parts of windows and doors, and on the metal fence.

Regardless of the type of future use of this station, the following work should be completed:

- painting of windows,

- painting of doors,

- paining of fence,

- painting of beams.

The concrete roof beams at this station are substantially damaged.  The top layer of concrete is missing in parts, so that the reinforcement is visible and partly corroded.

Externally, the concrete surfaces of the outer walls and the upper slabs of the channels are considerably damaged.

6.1.5  Ozonation station

This station is comprised of:

- an engineering room in which equipment is installed, and

- a tank in which chambers for the injection of ozone and the ozonation process are located.

There are four concrete platforms in the engineering room for ozone generators, which should be covered with ceramic tiles.  The entire station should be painted.

Externally, the concrete surfaces of the outer walls and the upper slabs of the channels are considerably damaged. In some places the damage to the channel walls has been repaired.

6.1.6 Chemical station

The entire structure, including metal fences, doors and radiators, should be painted.

  - Conclusions regarding proposed rehabilitation measures

The various structures of the plant have been in use throughout the period of operation of the plant.  In view of their function (hydraulic structures), the concrete surfaces of these structures are in permanent contact with water.  The most vulnerable is the top, protective layer which requires special attention.

The outer channels of the plant, which connect the filtration, pulsator and ozonation stations, have sustained most of the damage.

A special problem is the difference in the settlement of these structures (the filtration, pulsator and ozonation stations are structurally independent, their surface areas are different, as are the loads and the times of construction).

6.2.1 Repair of damaged concrete roof beams of the filtration and pulsator stations

The damaged surfaces should be repaired in full compliance with regulations which govern this type of work (repair mortar should be used, as necessary). Lower and side surfaces of the beams and, if possible, lower surfaces of the roof slabs, should be covered with Penetrat-based coatings.

6.2.2 Repair/rehabilitation of the existing supply channel to the filtration, pulsator and ozonation stations

In view of the function of the plant, the quality of the concrete should be tested (concrete grade and water-tightness).

The repair of joints and inner channel surfaces would require the plant to be shut down.  Since the plant can be shut down for only 2 to 3 hours, it will not be possible to undertake comprehensive channel repair and appropriate measures.  All available rehabilitation measures which will ensure non-interrupted operation of the plant are related to the repair of outer surfaces.

One exception is the crack along the working joint at the end of the channel (most threatened point).  Here the existing working joint will be rehabilitated as an expansion joint.  The water will have to be evacuated and the repair work performed on the inside as well.

7.  CONSTRUCTION OF THE FLOCCULATION STATION

7.1.  Foundation

The new structure is comprised of three separate structural units; two are exactly the same, and the third is used for the preparation of polyelectrolyte.

The polyelectrolyte preparation and dispensing unit will have strip foundations, 1.00 m and 0.80 m, while the flocculation structure will have a 50 cm-thick RC slab, as needed for the treatment process, foundation elevation -5.75 (247.10 m a.s.l.).

7.2.  Structure

The flocculation structure is comprised of an above-ground and an underground section.  The underground section is made up of two chambers: first flocculation stage (inner dimensions 6.0 x 6.0m), and second flocculation stage (inner dimensions 8.5 x 8.5m). The above-ground section is a reinforced-concrete skeleton structure with RC slabs and brickwork filling.

Tank walls are made from 40 cm-thick reinforced concrete.  The upper slab is at an elevation of ± 0.00 (252.85 m a.s.l.), 30 cm thick. The frame structure is comprised of beams (b/d/d1= 25/55/75 cm),  on roof overhangs b/d = 30/30 cm and b/d =40/165 cm in the longitudinal direction, and columns (30/40 cm).

The roof slab is a semi-prefabricated RC structure cast on the spot in formwork made from prefabricated beams. Blocks are TM-3, size 25x25x16 cm. The roof is covered with aluminium sheet and slanted at α = 12 ̊  (like the existing structures).

The construction of new structures will require a part of the slope to be cut, so the excavation should be appropriately protected. Consequently, a supporting wall should be erected along the entire length of the building facing the slope. The height of the supporting wall is 2.5 m.

  - Interior materials

All walls are made from red face brick, 25 cm thick.  The roof, roof edge covers and drainpipes are made from brown aluminium sheet.  Windows and doors are made from brown anodized aluminium.  The columns are visible on the facade, in architectural concrete, as is the skirting of the building.

Face-brick walls in the above-ground sections of the building are not plastered.  On the inside, they are joined in line with the wall so that the red brick is seen indoors as well.  The interior will thus have a high quality of wall finish in red face brick, which is pleasing to the eye and does not require any coating or maintenance.

The ceilings in the building are to be spackled and painted with white semi-dispersive paint.  Columns and beams of the frames remain in architectural concrete.  Embedded sections (chambers) are Penetrat-coated.

All floors of the dry sections of the structures will be covered with grey clinker ceramic tiles, as will the cantilever slab and slab face.

All inner and outer materials are high quality, durable, unchangeable, and require minimal maintenance.

Waterproofing of the structure (against moisture from the ground and from the water within the structure) will be comprised of Penetrat coats on the inside, which fill all cavities, crystallize and render the concrete impervious.

7.4.  Access road

The plant is located on a mild slope and is parallel to the isohypses in the northeasterly-southwesterly direction.  In order to facilitate access to the newly-designed structure, the existing dirt road within the plant grounds should be extended, widened and paved.

- GENERAL TECHNICAL CONDITIONS

I.  GENERAL TECHNICAL CONDITIONS FOR EQUIPMENT AND MATERIALS

8. General

These general technical conditions apply to hydro-mechanical and mechanical equipment of the Majdevo Water Treatment Plant.

Loading

Density – Dead load includes the weight of the structural members, equipment, mechanical assemblies, other parts, and protective coatings.  All steel parts and mechanical parts are assumed to have a density of 7850 kg/m3.

If not stipulated otherwise, each layer of protective coating should be assumed to have a weight of 3 kg/m2 of coated surface.

Water load – Water density is 1000 kg/m3. Hydrodynamic loads should be determined in each case separately, for exposed parts of equipment and structures.

Wind load – Wind load should be deemed to be horizontal. A wind pressure of V = 1000  N/m2 should be assumed for calm conditions. The wind attack surface is the surface obtained by parallel projection of the surfaces exposed to wind, on a single plane perpendicular to the wind direction.

Safety factors in respect of permissible loads and permissible stresses should be in compliance with JUS or DIN standards.

Materials

All materials used for the plant will be first-class and will be consistent in every respect with the most recent achievements in this area.  They must also conform to all the requirements specified in these Conditions.

Wherever stainless steel is used, it must be compact and free from cracks, impurities and layering.

Equipment for the plant must be simple, durable, of first-class workmanship, free from any hidden defects or faults, and based on most recent achievements in this area, such that it is reliable, durable in operation, and easy to maintain.

Wherever rivets and bolts are used, holes for them must be drilled accurately.  Parts joined or connected by rivets or bolts, which must be in accurately defined and in fixed positions relative to each other, must be drilled together to exact dimensions.  Wherever bolts and nuts need to be frequently adjusted or removed, they must be made from non-corrosive materials.

Sealing

All sealing elements will be made in compliance with applicable standards and regulations.

Parts embedded in concrete

All required stiffeners, base plates and anchors will be provided for parts and equipment embedded in concrete, to avoid any distortion or movement both during the casting of concrete and during normal operation.

Drawings

All as-built drawings prepared by the Contractor at the end of the work must accurately present all layouts, assembly details of all machines, equipment, instruments etc., in both elevations and cross-sections, functional schematics, and connection schematics, at a level of detail which is necessary to show the function, foundation structures, installation, operation and maintenance aspects.

Each drawing will include:  the scale, a legend of symbols used (if not standardized by applicable regulations), cross-references to other drawings, any subsequent corrections, etc.  Additionally, each component of a structure must be identified by an item number.

In addition to size, tolerance and symbol information, the drawings must include information about the type, quality and quantity of materials and clearly identify procedures for machining and thermal treatment.

All drawings must identify surfaces which are protected from corrosion.

For each part of the equipment or device which will be transported/moved by cranes, the drawings must clearly identify attachment/suspension points and include a schematic of how such components can be supported on a base or temporary supports during transport, to avoid any distortion or breakage.

  - Welding

In conducting welding work, the Contractor will comply with Yugoslav standards: JUS ISO 9690, JUS EN 287-1. These standards determine unique conditions for weld quality and identify requirements for shops or individuals in respect of welding work.

Weld joints will be made:

- by gas welding, in the case of pipes whose rated opening is  50 mm and whose size is  4 mm, and

- manual, electric arc welding with sheathed electrodes for pipes whose thickness is  4 mm

Welding is not allowed if pipe ends are wet or covered with ice, frost or snow.  Pipes should be dried and cleaned prior to welding.  Additionally, welding is not allowed if the work environment is not protected from rain and strong wind, as well as at ambient temperatures below –5 C. If the ambient temperature is between 0 and –5 C, preheating to + 50 C is required of a belt whose maximum width will be 50 mm. This temperature must be maintained during welding.  Ends to be welded together must be prepared by disk or autogenous cutting. All uneven spots, irregularities and oxide remains must be ground off.

Pipe ends should be cleaned to remove all traces of grease, oil, water, sand, varnish, rust, and the like.  The minimum length to be cleaned should be 25 mm from the end of the pipe.

When parts with different inner diameters are to be welded together, and if the difference is greater than 3 mm, the ends with the smaller inner diameters must be prepared from the inside (possibly ground) until a difference in diameters of less than 3 mm is obtained. If a part is welded to a non-machined part, there will be a 25% slant (relative to the internal generatrix parallel to the axis). The maximum reduction in thickness must not exceed the minimum design thickness of the pipe wall.

Pipe ends need not be prepared on the outside if the difference between pipe wall thicknesses is less than 30% of the thickness of the thinner pipe, but not more than 5 mm.  The weld joint will be prepared by gradual passes from the thinner to the thicker element.

If a pipe end acquires an elliptical shape during transport and if the thickness of the pipe is not greater than 10 mm, it can be repaired under cold conditions by means of special tools.  However, the magnitude of plastic distortion must not exceed 3% of the outer diameter of the pipe.

The centerlines of pipes prepared for welding must be in line.  This will be checked by a metal rod whose length will not be less than 400m. The tolerances are:

- 1 mm, for pipes whose rated opening is  100 mm, and

- 2 mm, for pipes whose rated opening is  100 mm

Welding will be conducted solely be certified welders who hold valid certificates for the required type of welding and the base material being welded.

Tack welding must be performed with first-pass electrodes. The same welder will do both tack welds and other welds of the joint.  Tack welds can become part of the joint if previously ground on both sides.  The spacing between tack welds should be roughly equal.  The number and lengths of tack welds are shown in the following table:

| Pipe diameter (mm) | Number of tack welds | Length of tack welds (mm) |
| --- | --- | --- |
| 25-50 | 2-3 | 5 |
| 75-300 | 4 | 12 |
| 350-500 | 6 | 20 |

In the case of butt welds, the first pass (root) must penetrate well but not more than 3 mm.

After each interruption of welding, the slag must be removed from the spot where welding will continue.  Additionally, any damage or irregularities must be eliminated. It is recommended that the first welding pass be completed without interruption.

For pipes whose thickness is  4 mm and the rated opening is up to 50 mm, gas welding is allowed and at least two passes are required.

Following the first pass, the joint will be filled by means of manual electric arc welding.  While filling, each layer must be carefully cleaned to remove slag and any irregularities ground off.

Following welding, butt welds can be higher than the edge of the pipe by:

- max 2 mm for pipe thickness  12 mm

- max 3 mm for pipe thickness  12 mm

Each welder shall place his identification on the weld he has made.  Two welders cannot have the same identification even if they do not work at the same time.

The shape and size of welded elements can be adjusted by mechanical means such as grinding, milling, polishing, autogenous cutting or electric arc cutting, to meet requirements.  Welding metal selection must comply with approved standards and allow for deep penetration and good bonding with the base material.  Edges of surfaces to be welded must be made from healthy metal, with no visible damage or damage due to cutting, at a minimum distance of 50 mm from the weld edge.

8.2.	 Deliverables

8.2.1. General

The purpose of these Technical Conditions is to define the hydro-mechanical equipment and machinery for the WTP to the level of detail required for the Bidder/Manufacturer/Contractor to prepare its bid and to fabricate, transport, install, test and put the equipment and machinery into operation.

8.2.2. Scope of delivery

These Technical Conditions are related to the following work:

-	preparation of documentation, instructions for shop inspection of equipment and materials, instructions for functional and acceptance testing, instructions for operation and maintenance,

-	any revision of the documentation in consultation of the client,

-	purchasing of materials and presentation of certificates of compliance,

-	fabrication, in-shop application of corrosion protection, and packing of equipment,

-	transportation, installation and putting of the equipment into operation.

The above work pertains to the following equipment:

-	ozone generator

-	ozone destructor

-	pump units

-	flocculator

-	valves and fittings

-	pipeline

-	spare parts

-	installation tools

8.2.3. Delivery schedule

The Contractor/Manufacturer will prepare the technical documentation, purchase materials, fabricate, ship, install and put the deliverables into trial operation within the time frame defined in consultation with the Contracting Authority/User.

8.2.4. Limits of delivery

The limits of delivery are defined by this project.

8.2.5. Complete delivery

The delivered equipment must be complete and include all devices and parts in order to function safely and faultlessly regardless of whether all the details have been addressed in these Technical Conditions or not.

8.3.	Requirements related to mechanical equipment

The Manufacturer/Supplier will deliver, install and put into operation the following:

- Ozone generator

- Two ozone destructors, type COD-43 or similar

- Two centrifugal pumps, type LS 400-400 or similar.

8.3.1. Mandatory characteristics of the equipment

8.3.1.1 Ozone generator

The system must be produced in compliance with stringent, generally-recognized international standards (e.g., DIN 19627). The operating concept will be high voltage electrical discharge with thyristor-based frequency controller.

Basic characteristics of the ozone generator:

- Number of units					1 + 1

- Ozone generating fluid				oxygen

- Design capacity					5.4 kg/O3/h

- Design O3 concentration

(for a cooling water temperature of 5C)		179 g/m3

- Design O3 concentration

(for a cooling temperature of 25C)		148 g/m3

- Operating gas pressure				1.2 bar

- Output pressure					0.9 bar

- Max. cooling water temperature			25 C

- Amount of cooling water				5 -10 m3/h

- Cooling water pressure				1-4 bar

- Oxygen pressure				4-6 bar

- Power supply					400 V/50 Hz/3Ph/N/PE

- Materials:

- Parts in contact with gas			304 ss/316 LSS/316 Ti

- Parts in contact with cooling system		316 LSS/316 Gi

8.3.1.2 Ozone destructor

Technical characteristics:

- Number of units			one operating + one standby

- Type				catalytic, preheated COD

- Preheating			electrical

- Gas flow			up to 43 Nm3/h

- Input temperature		20C

- Control				relay-based

- Installed power			0.27 KW

- Installed fan power		0.65 KW

8.3.1.3 Filter backwashing pumps

The pump shall be similar to LS 400-400 and shall have the following characteristics:

- Q = 228 l/s

- H = 8.7 m

- P = 30 kW

Over their operating range, the pumps must operate without cavitation or instability. The hydraulic power at the pump shaft, over the entire operating range from 0 l/s to 320 l/s, must not exceed 30 kW.

8.3.2. Controls, signaling and protection

Filter backwash pumps are automated, but can also be controlled manually either on the spot or remotely from the CC.

Filter cleaning pumps and compressors are controlled based on:

- filter operation

- required water and air flow

- flow rate achieved by the pumps and compressors

- water level of intake basin

- water level of filters

- number of hours of operation of individual pumps

All data are entered into a control processor and may be modified, as needed.

Any pump or compressor fault is signaled to the CC, and the role of the pump or compressor is assumed by the standby unit.

For manual control, the operator will remotely from the CC (or on the spot based on CC instructions) start the required combination of pumps.

The water level in the pumping station intake basin will be measured by means of a continuous flow meter.  Water level sensors will be located in a vertical pipe in the basin. The water level signal is transmitted to the CC and used to monitor and control the operation of the pumping station.

Detailed information about the pump/compressor station is included in the Electrical Part (power supply and controls).

8.3.2.1 Automated operation of the pumps

Pump on/off control is based on the water level of the tank via a continuous flow meter installed in the tank.  A frequency controller will regulate the flow. The overriding control parameter for pump shutdown will be the water level which protects the pump from dry running.

8.3.2.2 Local pump control

In addition to automated operation of the pumping station, the pump units can be started and shut down by means of pushbuttons in the dedicated control cabinet.

8.3.2.3 Signaling and protection

The following local signals will be provided for each pump in the control cabinet:

-	pump on/off

-	pump failure (cumulative signal)

-	minimum operating level

-	dry run protection

The following pump protection/locking will be provided:

-	dry running

-	minimum operating level – both pumps shut down

-	loss of phase

-	overload

- phase asymmetry

- thermal protection of bearing windings

- protection of motors from moisture penetration

8.4.	Pipes and pipe connections

Basic pipeline characteristics are defined in the graphic documentation. Corrosion protection will be provided in accordance with Section 6 of the design.

8.4.1. General

The Contractor will purchase, deliver, install and test all pipes, connectors and ancillaries in accordance with the drawings and these requirements.

The lengths of the delivered pipes will be appropriate for installation and as defined in the design (drawings and specifications), keeping in mind minimum weld joints. Each pipe will be clearly identified, including the name of the manufacturer, rated diameter, weight per meter, and operating pressure.

If a butt weld is required, the pipes will be cut at an angle to the outside, based on applicable regulations.

Seals of flanged joints will be rubber rings, reinforced with fabric.

Flanged connections will be bolted.  The numbers and sizes of bolts will be per JUS standards, or ISO x 2084 standard, the same as the flange.  Bolts will be zinc plated.

Each portion of the supply will be accompanied by a manufacturer’s certificate of compliance with JUS standards.

The Contractor will protect all pipes and liners with coatings, against damage during handling and transportation.  Pipe ends will also be suitably protected.

All pipes and ancillary components will be adequately supported to prevent any deformation of the equipment.  The Contractor is required to certify that this requirement has been fulfilled.

Indoor pipes will be suitably anchored and supported from the floor. The shape of pipe supports will be adequate for the respective pipe.

Unless specified otherwise, all pipes operating under pressure will be tested.  The lengths of the pipe section to be tested are subject to approval.  For these tests, the Contractor will make available the required pumps, temporary plugs or covers, pressure gages and other equipment (as required), clean water and labor, at no extra cost.

When pressure testing the pipes, the Contractor will raise the water pressure by pumping (relative to the lowest point of the tested section of the pipe and adjusted relative to the gage location) until a pressure in bars is reached which is numerically equal to the level of the test pressure inside the pipe.  If the Contractor cannot reach the specified pressure, or maintain such pressure for one hour, the tested section will be deemed not to have passed the pressure test.

Following successful pressure testing of the pipes, the Contractor will conduct a leakage test.

If any section fails to pass the pressure test or the leakage test or both, the Contractor will do everything that is required to locate, repair or relocate the defective pipe, valve or fitting, at its own cost and without delay relative to the agreed time schedule.  Additional tests and repairs will be conducted only after the section has passed the tests defined in these Technical Conditions.

Steel pipes will be connected by welding and then anti-corrosion coatings will be applied.

8.4.2. Pipe connections

The steel pipeline and stainless steel pipes are intended for an operating pressure of 2.5 bars and a test pressure of 4 bars.

Č.0361 steel will be used to fabricate steel pipes. These pipes will be welded spirally or longitudinally.  Steel pipes used for this project will have standard pipe wall thicknesses:

DN 800	  812 mm		 = 8.0 mm		G' = 158 kg/m'

DN 700 	  711.2 mm		 = 7.1 mm		G' = 124 kg/m'

DN 600 	  609.6 mm		 = 6.3 mm		G' = 94.1 kg/m'

DN 250 	  267 mm		 = 5.0 mm		G' = 32.3 kg/m'

DN 200 	  219 mm		 = 4.5 mm		G' = 23.7 kg/m'

Stainless steel pipes will have ISO/Metric dimensions per the EN 10217 or EN 10216 standard.  Tolerances will be consistent with the EN ISO 1127 standard.

8.5.	Valves and fittings

8.5.1. General

All valves and fittings to be installed on the WTP pipes must comply with standards applicable to the production of valves and fittings.

Valves and fittings will be appropriately identified (DN, PN), and will show the direction of fluid flow.

Water tightness at nominal pressure and resistance to internal pressure at test pressure will be bench tested by the manufacturer in the presence of representatives of the Contracting Authority/User.  Tests will be conducted per the JUS.M.C5.013 standard (tested per EN 12266).

Flange connection dimensions will comply with the JUS.M.B6.011 (EN 1092) standard for the respective rated diameter and pressure.

Valves and fittings delivered for installation will first be inspected in detail.  Mechanically driven valves and fittings (driven manually or by means of an electric motor) will also be functionally checked.

Operating parts of all valves must be replaceable and coated with materials certified for drinking water.

The operating mechanism must be provided with lubrication devices.

All valves must be lockable in their open and closed positions. Each valve will have a name plate.

All manually driven valves will be closed clockwise, by means of a turnwheel which must be marked to show the direction of closing.  Valve turnwheels must be adequately installed for easy access and operation.

Flanges must be machined over the entire surface extending to the inner diameter of the pipe.  The flanges must be concave to ensure a perfect straight line, with rubber O rings placed in appropriate grooves.

8.5.2. Butterfly valves

Acceptance of valves will take place at the supplier’s shop in conformity with the JUS M.C5.013 standard (or EN 593) and tested in accordance with EN 12266 for drinking water.

All butterfly valves will close clockwise.

For all types of butterfly valves, manufacturers will present graphs showing the pressure drop curve as a function of percent opening, including a formula which can be applied to calculate real pressure losses.

Valves will be supplied with all necessary nuts, bolts and seals.

8.5.3. Gate valves

Gate valves will comply with the DIN 3352 standard.

8.5.4. Check valves

A check valve is to be installed on the discharge line of the filter backwash pump.  The check valve will close by the action of the return flow of water.  Check valves will be delivered together with the pump unit and must be watertight upon installation.

8.5.5. Dismantling pieces

Dismantling pieces are used as connection elements since they facilitate installation of valves and allow for installation lengths to be adjusted to +/- l.

8.5.6. Flow meter

A DN 600 electromagnetic flow meter will be installed on the DN 600 filter backwash water pipe.  Its measurement range will be 0 – 500 l/s.

8.5.7. Pressure gages

Pressure gages must be fabricated in compliance with standards approved by regulations (JUS.L.H1.004.).

Each pressure gage must be equipped with a shutoff valve, adjacent to the pressure gage, and each pressure pipe must be outfitted with an isolating valve at the point of connection to the main pipe system.  If pressure gages are panel-mounted, the valves must be suitable for connection of a test pressure gage.

Pressure gages which are not panel-mounted must be chromed.  If there is a difference between the level at which the pressure gage is located and the point at which pressure is to be measured, appropriate compensation will have to be made at the time the dial is read, on which the amount of this compensation must be marked.  If the compensation is 2% (or less) of the entire normal operating range, this compensation can be disregarded.

If practicable, pressure gages will be panel-mounted, on locations approved by the Employer.

Valves which block the pressure gages must be clearly identifiable via name plates of approved type and lettering.

8.6.	Inspections and testing

8.6.1. Pump units

8.6.1.1. Testing of pump characteristics

Pump characteristics will be tested on a test bench (of the pump manufacturer or a company that has the appropriate equipment), in accordance with applicable regulations

- JUS M.F1.021 CLASS B (ISO 3555 - CLASS B)

- DIN 1944. Comparison of measured and guaranteed characteristics will be based on Class II accuracy.

Over the entire operating range, the pumping power must not be greater than the guaranteed maximum power (i.e., 30 kW).

Over the entire operating range, the pump must operate with no cavitation or instability.  Vibration must be within permissible limits, up to 8 mm amplitude (for 50 Hz).

8.6.1.2 Testing under steady state conditions

These tests include:

- testing and calibration of the flow meter on the discharge line,

- determination of Q, H, and h for each pump in at least one point,

- determination of Q, H and summary h of the pumps in parallel operation,

- determination of vibrations of the electric motors of the pumps in three directions:

- in the direction of the pump axis,

- perpendicular to the axis, in the direction of the discharge line,

perpendicular to the axis, perpendicular to the discharge line.

8.6.1.3 Testing under regular transient conditions

These tests will include:

- regular starting and stopping of each pump separately,

- regular starting of all pumps, one after the other, until the nominal flow rate of the pumping station is achieved,

- regular stopping of all pumps, one after the other, after the nominal flow rate of the pumping station has been achieved.

During the tests, the following will be monitored and recorded as a function of time:

- RPM variation of one pump,

- change of valve position at the discharge end,

- vibrations of electric motors,

- flow,

- discharge pressure,

- intake basin water level.

8.6.1.4 Testing under emergency/accident conditions

Within the scope of these tests, pump failure is simulated by sudden intentional shutting down of power supply.

The test procedure is as follows:

- First the failure of each pump is simulated separately and the following parameters are monitored:

- RPM,

- flow,

- discharge pressure,

- intake basin water level.

Then failures of the pumps are simulated.

Following each failure, test results should be analyzed on the spot and an appropriate decision made regarding the continuation of the tests.

Prior to the test, a detailed test plan and program must be prepared and formally approved by the Contracting Authority.  It is desirable to have the tests conducted by an experienced and established team of specialists in close cooperation with the future user’s personnel.

A test report must be prepared upon completion of testing.  It must include test descriptions and records, as well as conclusions regarding the behavior of the pumping station.

8.6.2. Inspection and testing of shapes, sizes and machining

All major components of the pumps will be subjected to testing, including: shaft, suction basket, impeller and wet elbow.

The quality of the incorporated material must comply with design requirements and applicable standards; certificates of compliance will be presented as evidence.

For thermally treated parts, the manufacturer will present to the Purchaser’s inspector(s) thermograms or other evidence, while for welded parts the manufacturer will familiarize the Purchaser with applied welding technologies and present certificates for the additional material used and welder certificates.  If any repair has been undertaken, repair schematics and reports will also be submitted.

Additionally, a measurement sheet will be presented, including the results of inspection of shapes and sizes.

The Purchaser’s inspector(s) will conduct the following at the Contractor’s shop as well as during installation:

-	a review of the above-mentioned documentation,

-	visual inspections,

-	inspections of shapes and sizes,

-	inspections of welded joint quality

-	inspections of the quality of machined parts

-	inspections of anti-corrosion protection

-	functional tests

-	guarantee tests

8.6.3. Pipe weld testing

Tests will be conducted by the Supervisor appointed by the Contracting Authority. Welding inspections will be performed by the Contractor’s inspectors.  The Supervisor will request and obtain insight into all welder certificates for the respective welding procedures.  The Contractor must maintain documentation on each inspection of welders and welded joints performed.  All tests and test methods must be properly documented and certified by the individual or individuals who have performed the tests.  Each test which was not passed must be repeated on the same spot following repair of the defect.  The spot to be inspected will be selected by the Contracting Authority’s Supervisor.

Tests will be conducted using non-destructive methods.  If so required by the Contracting Authority, destructive methods may also be used.  Carbon steel pipes will be subjected to the following inspection/testing:

- visual inspection, and

- x-ray testing of the welds.

X-ray testing will be conducted in conformity with JUS ISO 5579, JUS ISO 1106-3. Radiation sources, films, foils and other quality indicators will be used.  Quality indicators must comply with JUS ISO 2504. The sensitivity of each image must be such that any defect whose minimum size is 3% of the thickness of the irradiated layer must be discernible.  Images will be evaluated by a certified organization which will prepare a written report.  The report will include information about the location of the work undertaken on the pipe, the welder, image number, size and type of defect, and evaluation of test results.  The test scope for all welds is 100%.

8.6.3.1 Weld errors

Cracks and putting unprepared - cold braze will not be allowed. Unbrazed root or incomplete bonding will be allowed only if the defect is not larger than 0.8 mm or 20% of the pipe wall thickness (whichever is smaller).

Reinforcement or incavation of  braze head:

- The permitted reinforcement of braze for a wall thickness up to 12 mm is a maximum of 3 mm or 33% of the wall thickness (whichever is smaller)

- The permitted incavation of braze head is up to 0.8 mm or 12.5% of the wall thickness (whichever is smaller)

Porosity:

- The weld can be porous in places provided that their size does not exceed 2.4 mm or 50% of the wall thickness for its largest dimension.

- The total porous surface, projected radially to the weld, cannot exceed three times the largest individual porosity error for any 6cm2 of the weld surface

Foreign bodies:

- The length of any one foreign body must not be greater than twice the pipe wall thickness.

- The width of any foreign body must not be greater than 2.5 mm, and the length of all foreign bodies must not be greater than four times the wall thickness for a 152 mm length of the weld.

- No tungsten is allowed.

Repair of defects

- All defects assessed as unacceptable must be eliminated.

- In the case of carbon steel, this will be done by autogenous cutting and grinding of the joint, or grooving and grinding of the joint.

- In the case of pipes whose rated opening is  2”, the entire joint will be cut out, while in the case of larger-diameter pipes only the defective spot will be cut out.

- Following each repair, the same spot will be inspected again, following the same procedure which was used when the defect was uncovered.

8.6.4.	Piping installation test using test pressure

Following installation and prior to putting into operation, the piping installations must be tested using test pressure. The purpose of this test to establish whether the installations and watertight and stable.

- The water tightness of the piping installations will be tested to internal pressure. The filter air scouring pipeline will be tested by pressurized air.

- Water distribution pipes will be tested as follows:

- -	Preliminary test – operating pressure 2.5 bars

- -	Main test – operating pressure 4.0 bars

- The filter air-scouring distribution piping will be tested as follows:

- The water pressure test procedure will include the following steps:

- 1. Filling of the piping

- 2. Preliminary test

- 3. Main test

- 4. Flushing and disinfection of the piping

- All supports and stiffeners of the respective piping must be installed prior to the test.  All joints must be free and accessible.

- Filling of the piping and evacuation of air

- Filling will commence following completion of installation of the piping, including supports and stiffeners. A small amount of water will be used to ensure satisfactory evacuation of air.

- Appropriate valves will be opened/closed to isolate the pipe section to be tested.

- Air outlet valves and water inlet valves will be prepared for the test.

- The piping will be filled from the lowest position at a rate of 0.05 m/s.  Prior to the test, the piping will be filled with water for at least 24 hours.

- Prior to filling (and after the piping was charged for 24 hours), another inspection should be performed to ensure that all air has been removed from the piping.

- Preliminary tests are conducted to check all joints and other parts of the piping.

- Preliminary tests of steel piping will be conducted at the maximum operating pressure.

- If preliminary tests show that any part of the piping or joint is leaking, the pressure will be increased to test pressure to clearly show all weak points of the piping.

- After all weak points have been recorded, appropriate repairs will be undertaken.  Repairs can only be made when the piping is not pressurized or is empty (to be decided by the Supervisor).

- Main test

- The main (trial) test will be conducted immediately upon completion of the preliminary test.  Each joint will be inspected.

- Duration:  The test will last for as long as required to inspect each joint in detail and note any change or distortion of the pipeline, however small.  The test will be conducted at low temperature fluctuations.

- NOTE:	In exceptional cases, the duration of the test can be reduced upon approval of the Supervisor.  However, the pressure will not be increased to reduce the duration of the test.

- During the test, pressure will be recorded by a calibrated pressure gage.  Two pressure gages will be used.  The pressure gage will be such that it allows for reading of one meter of water pressure (0.1 bar).

- The pressure gage will be positioned at the lowest point of the piping.

- During the test, water will not be added to adjust the pressure.  The piping will be deemed compliant if during the main test the water pressure does not drop by more than 0.1 bars.  If the test pressure cannot be reached, the joints will be inspected.

- A record of the pressure test must be kept.  The test report will be signed by designated representatives of the Contracting Authority and the Contractor (a representative of the Contracting Authority must witness the test to inspect the piping and pumps and ensure that no unauthorized pressure adjustments are made).

8.6.5. Valves and fittings

All valves and fittings will be checked applying a test pressure which is 1.5 times higher than nominal, to demonstrate the quality of the housing.  The test will also be conducted at the rated pressure to check for any leaks.  Certificates of compliance will be presented to the User.

8.7.  Guarantees

8.7.1. General

All required materials and stipulated characteristics of the equipment defined in Section 8.2 of these Technical Conditions are deemed to be guaranteed.  If the required quality levels and values are not demonstrated during the tests, the User is entitled to reject or reduce the price of non-compliant equipment or part thereof.

8.7.2. Guaranteed characteristics

The following will be deemed to be guaranteed characteristics:

Pump units:

-	Head (Q-H)

-	Efficiency (Q-ETA)

-	Power (Q-P)

-	No cavitation or vibration

8.8. Packing

8.8.1 General

All equipment will be properly packed to avoid damage or loss in transit or while in temporary storage prior to installation.  Packing will be suitable for transportation by truck or van.  Each consignment will be accompanied by a packing list.

8.9  Installation

8.9.1. Scope and limits of installation

Installation includes storage of equipment at the site, local transportation, assembling at the point of installation, and actual installation.

The Contractor will install all the equipment which falls within the scope of these Technical Conditions, and will install and adjust all parts embedded in concrete (pump supports and the like).  The Electrical Contractor will supply and install all power supply cabling for pump motors, main motor start probes, and indication and signaling devices located in the control cabinet.

8.9.2. Organization of installation

Installation will commence upon completion of construction and finishing work.  An auto crane, hooks and tirfors will be used for unloading, transportation and installation.  In addition to hooks and tirfors, standard and special tools supplied with the equipment may also be used for installation purposes.

8.9.3. Tests during and after installation

The following tests will be performed:

- Inspection of the system for completeness, including testing of nut and bolt tightness,

- Testing of anti-corrosion protection,

- Filling of the system with water, leakage tests, and functional tests of all valves under still water conditions,

- Testing of pump/compressor station piping to hydraulic pressure

- Inspection of equipment adjustments

8.10.  Spare parts

Spare parts will be recommended by the equipment manufacturer.

8.11.	Tools

8.11.1. Standard tools

Tools which comply with the requirements stipulated by the equipment manufacturer will be supplied for installation and maintenance of pumping station equipment.

8.11.2. Special tools

The manufacturer of the equipment will provide a recommended list of special installation, dismantling and maintenance tools, including prices.

8.12.    Takeover of equipment

8.12.1.  General

Following installation of electrical and mechanical equipment and completion of construction and finishing work, a Technical Acceptance Committee will be formed pursuant to the Construction Law of Serbia. The takeover of mechanical equipment will include the following activities:

8.12.2. Test operation

Following installation, dry or wet tests will be conducted to demonstrate the functioning and guaranteed characteristics of the equipment.

The tests will confirm that the materials, characteristics and functions of the equipment comply with design requirements and applicable standards. The Contractor will submit all test results to the Project Manager for approval.

Unless required otherwise by the Project Manager, all shop tests, test during and after installation, and acceptance tests will be conducted in accordance with applicable standards.  If no standard is available for a particular test, the scope of and method to be applied for such a test will be proposed by the Project Manager.

The Contractor will provide all standard ancillary instruments and other measuring equipment required for all the tests.

8.12.3. Trial operation

Trial operation will follow the completion of test operation and will last for 3 days.  During this period the equipment must operate faultlessly.  The Contractor will complete as-built drawings during this time.

8.12.4. Preliminary acceptance

Upon successful completion of trial operation, the Contractor and the User will perform preliminary acceptance.  In addition to equipment and material test reports and certificates of compliance, an Operating and Maintenance Manual, spare parts, and tools will be presented to the User.

8.12.5. Technical acceptance

Following preliminary acceptance, the Technical Acceptance Committee will proceed with the technical acceptance of the plant.  All the preliminary acceptance documentation will be presented to the Committee.  The Committee may require some of the functional tests of the equipment to be repeated.

9.  ANTI-CORROSION PROTECTION

In view of the environment in which the hydro-mechanical equipment will operate, special attention must be devoted to anti-corrosion protection.  In particular, none of the means of protection will contain toxic substances.

Protection of the equipment is divided into protection of inner and outer surfaces.  Protection of outer surfaces from corrosion is sub-divided into active and passive protection.

Anti-corrosion protection includes:

1.	Preparation of surfaces

2.	Application of base and top coats

3.        	Inspection of the quality of the work

Anti-corrosion protection is applied in the equipment supplier’s shop and at the site, before and after assembly or installation.

In the shop, the manufacturer will perform sand blasting and apply a base coat and the first top coat.

The purpose of this anti-corrosion protection is to protect the equipment in transit and during installation, and is included in the ex-factory price of the equipment supplied by the manufacturer.

At the site, upon completion of installation, the anti-corrosion protection applied in the supplier’s shop will be repaired, as appropriate, and then the remaining top/final coats applied.

Upon completion of welding at site, installation welds will first be cleaned to metal shine and then complete anti-corrosion protection applied (both shop/primary protection and final protection).

9.1 Anti-corrosion protection method

9.1.1 Sand blasting – to metal shine, i.e., until all impurities, iron oxide (FeO and Fe2O3), (Fe3O4) and slag have been removed.  Sand blasting will be performed using special compressed-air units in full compliance with the EN ISO 8501-1 standard.

9.1.2 Base coat – applied on prepared surface within no more than 8 hours after sand blasting, suction and inspection.  The base coat may be applied at an ambient temperature between +50 C and +400, and a relative humidity of 75%.  The Supervisor must be consulted if the percentage is higher.  The base coat will be left to dry for at least 4 hours.

9.1.3 Top coat – applied over the first, dry coat, in the same manner as the first coat.  The second coat will be left to dry for 48 hours.

9.2 In-shop anti-corrosion protection of steel piping:

9.2.1 In-shop outer protection of steel piping:

- Sand blasting SA 2 and ½  EN ISO 8501-1.

- Base coat:  epoxy resin containing iron, dry coat thickness min. 1x80 m

- Top coat: polyurethane containing iron, dry coat thickness min. 1x80 m, approved for raw ozonated water.  Preferred color blue, RAL 5002.

9.2.2 In-shop inner protection of steel piping:

- Sand blasting SA 2 and ½  EN ISO 8501-1.

- Base coat:  2 layers of epoxy resin containing zinc phosphate, dry layer thickness2x50 m

- Top coat:  2 layers of epoxy resin, dry layer thickness 2x35 m, 
approved for raw ozonated water.  Preferred color blue, RAL 5002.

9.3 Anti-corrosion protection of VALVES AND FITTINGS:

9.3.1 Outer in-shop protection of steel piping:

- Sand blasting SA 2 and ½  EN ISO 8501-1.

- Base coat:  two layers of primer rich in zinc or two layers of zinc phosphate, dry layer thickness   0.1 mm

- Top coat: 2 layers of epoxy resin, dry layer thickness  0.07 mm, approved for raw ozonated water, preferred color blue - RAL 5002.

9.3.2 In-shop inner protection:

- Coating approved for raw ozonated water, preferred color blue - RAL 5002

9.4 Protection of concrete surfaces

Following sand blasting or cleaning with steel brushes, surfaces lying in concrete will be coated with cement milk.  The cement milk will be prepared manually and the following formula will be used:

- cement M40				100 parts by weight

- sodium nitrate (NaNO3)    	10    "        "

- casein resin 	 		10    "        "

- water                           	 	20  to 35    "        "

Prior to application, this mixture must be stirred well and used within no more than 3 hours (after 3 hours it is not useable).  One layer will be applied.

9.4.1 Storage of materials

Materials will be stored in dry rooms.  The minimum permissible temperature is +/- 20 C. Paint/coat containers must be sealed by the manufacturer and stored unopened.  The following information will be clearly marked on each container:

- Manufacturing date

- Lot/batch

- Number of certificate of compliance

- Expiry date

The storage room/area will be adequately protected from fire in accordance with applicable regulations.

9.4.2 Warranty

A five-year warranty will be granted from the date of technical acceptance and putting of the equipment and devices into operation.

II. TECHNICAL TERMS FOR CONSTRUCTION WORKS AND SPECIALIST’S TRADES

10. EARTH WORKS

10.1 Field clearance and topsoil removal

10.1.1 General

Field clearance will be performed in the area where the construction works are going to take place as shown on drawings, or in the area determined by the Site Supervision.

Field clearance comprises of the following:

Clearance from bush wood, weed and other plants. Tree stumps are to be dug out and the field leveled afterwards, i.e. the holes filled with the material approved by the Site Supervision.

Removed plants are to be classified and transported to a place determined by the Site Supervision.

All the materials remained after field clearance are in the possession of the Employer.

Topsoil removal will be performed in the areas shown on drawings or in the ones determined by the Site Supervision.

Topsoil will be hauled to a particular stockpile wherefrom it will be used for top soiling of areas to be grassed, or if it is taken from agricultural land it will be returned to the same place.

10.1.2 Payment

Field clearance from bush and trees including stump removal and hole filling will be paid as per agreed unit rates per meter of cleared surface.

Topsoil removal will be paid as per agreed unit rates for square meter of the removed topsoil.

The agreed unit rate includes the excavation and hauling to a topsoil stockpile as well as its management.

10.2 Excavation

10.2.1	General

The Contractor is under obligation to perform all necessary preliminary works for the excavation such as: setting, maintenance and removal of necessary installations and equipment, electrical supply for starting the equipment and lighting, draining, water pumping, construction roads, gauges, connection lines and any other necessity defined by the Programme of works and execution plan approved by the Site Supervision.

The costs of all necessary preliminary works must be included in the unit rate for the excavation works.

The Contractor is under obligation to conduct the works in accordance with drawings, these Technical terms and in accordance with the instruction of the Site Supervision.

The work includes the supply of all materials necessary for the construction, hiring the manpower and equipment, works on the excavation itself, transport of the excavated material, possibly placing of supports and various types of scaffolding, as well as the supply of all other materials necessary for the works in question.

10.2.2	Classification

The excavation is classified by:

- The type of the excavation:

- wide excavation

- narrow excavation

- The type of the excavated material:

- earth material

- stone material

The type of the excavation

Wide excavation refers to construction foundations and to removal of materials from wide areas. This item is applicable to all excavations that are 5m wide and more in the level of field.

Narrow excavation refers to the ones that are narrower then 5m in the level of field. This type of excavation is for foundations, various channels, ditches for pipe or cable placing and other. The supposition is that the excavation would partially be manually conducted. In case vertical excavation or any other type of excavation that the material cannot hold, is required, either by the Design or ordered by the Site Supervision, proper strutting method is to be applied, i.e. cut support is to be made. The Contractor will give the proposal on strutting method that must be approved by the Site Supervision prior to its application. The Contractor bears the responsibility for work safety and technical solution correctness even when strutting was performed as required and/or approved by the Site Supervision.

Ditches would be widened in the places of water pipes welding, shafts or wherever required by the Design. The widening will mainly be performed manually.

The type of excavated material:

“Earth materials” is common name for all excavated material types that are performed either manually or mechanically without blasting. Removal of any individual stones smaller then 1m found in the material of this type is not subject to additional payment. The excavation of this type (according to Stiny) in civil engineering falls into II-IV category.

10.2.3	Method statement

The term excavation refers to mechanical and manual excavation, mechanical removal of the material and hauling to either a place where it will be used or to a stock pile. All excavated material should be classified per quality in accordance with the Design and these Technical Terms.

All excavations should be conducted on cross-sections, levels and grid bearings from the design, or as per requirements of the Site Supervision. The work also consists of cleaning of areas in the earth material which require special protection measures, such as securing of degradated zones, pockets, water springs and other.

During the excavation, the Site Supervision will make possible changes in slope grade depending on material properties, geological conditions and other factors the Contractor must take into consideration during the construction.

Special attention should be paid during work execution that there are no slope failures. If any such case does occur, the Contractor’s responsibility is to mend the slopes as instructed by the Site Supervision without any right to claim.

10.2.4 The use of the excavated material

The Employer is in the possession of excavated material. It is used for the construction in accordance with the Design and the instructions of the Site Supervision.

All residual material must be hauled to stock piles as decided by the Site Supervision or used for ditch filling or any other hole filling in the field. If there is still residual material after the filling, it must be hauled to stock piles.

10.2.5	Excavation tolerances

The discrepancy in dimensions between the design and executed excavation can be:

- for the excavation of dry material +10 cm and -5 cm

- for the excavation under water +20 cm and -10 cm.

In case the Contractor does not execute works within the allowed tolerances, he will rectify all irregularities as ordered by the Site Supervision, at his own expense. If the excavation is within the tolerances, there will be neither additions nor deductions and the payment will be as per designed measures.

10.2.6	Transport

The material is to be transported using the shortest way between the site and embankment or stock pile. Public roads will be used for transport unless any others are approved by the Site Supervision.

All the expenses that may occur as a consequence of the transport on the route that was not approved are to be covered by the Contractor.

The expenses of the construction and maintenance of the access roads and ramps are to be covered by the Contractor.

10.2.7	Measurement and payment

The quantities of the excavated materials are measured in meters of autochthon material. The bases for measurement are cross-sections surveyed prior and after the excavation as per Design and changes approved by the Site Supervision. Cross-sections are valid only after signed both by the Site Supervision and the Contractor.

Payment of the excavation is based on unit rates for certain items of the excavation.

The cost includes the excavation, managing and cleaning of all slopes and critical points, all required strutting, all material required for blasting and for water pumping.

The cost of transport includes loading and unloading of the material at the place of construction or the stockpile.

All other expenses caused by the excessive excavation or transport via longer route and without the approval from the Site Supervision will be covered by the Contractor including the compensation for the destroyed land and plants, as well as any other damage caused in the process.

10.3.	FILLING

10.3.1	General

The Contractor is under obligation to perform all necessary preliminary works before the filling such as: placing, maintenance and removal of necessary installations and equipment, electrical energy distribution for starting the equipment, construction of site road and any other requirements from the Site Organization Plans and execution plan approved by the Site Supervision.

The costs of all required preliminary works must be included in the unit rate for filling.

The Contractor is under obligation to perform the filling works in accordance with drawings, these Technical Terms and Site Supervision’s instructions.

The work comprises of the delivery of required material for filling, hiring manpower and equipment, material transport, filling, compaction and leveling.

10.3.2	Classification

The works specified in this chapter are divided into:

N 1 Dredging of sand

N 2 Backfilling of foundations and trenches after executed works

N 3 The construction of sand bed

N 4 The construction of gravel base under the structure

N 5 The construction of vertical gravel drainage system around the structure

10.3.3	Method and scope of works

Backfilling of foundations and trenches (item N 2)

The chapter refers to the following works:

- filling the foundation pits after founding

- filling the trench where pipe and cable conduits and similar are placed

10.3.4	Backfilling of foundations and trenches

After concreting works or placing of conduits and other equipment have been finished, already excavated and temporarily stored material will be used for trench or foundation pit filling after which it will be spread, compacted and treated in accordance with the design and these Technical Terms.

Larger stone pieces, of any size, will be removed from the chosen material used for foundation filling.

For trench filling where the pipes and cables are placed, all stones larger than 5cm must be removed from the material that will fill the trench in the layer of at least 30cm above the pipe (and cable).

The material will be placed in layers of 30cm in thickness, which will be compacted using manual compaction equipment paying special attention not to damage the pipe, cable or wall insulation. After backfilling conduits/cables with the first layer of 30cm, the material can contain larger stones, placed in thicker layer and larger compacting equipment can be used.

The contractor is warned that no backfilling can start before the required pipe testing is performed and the concrete in anchor blocks and bench marks reached the required strength (about 7 days old).

In case the excavated material does not conform to the aforementioned requirements, the Contractor’s obligation is to fill the ditch using the material from the borrow pit, as approved and ordered by the Site Supervision.

10.3.5	Finishing filling layer

In case the trench is placed beneath carriageway construction, the surface must be compacted to at least Me= 400kp/cm measured by i30cm plate.

In case the results show the backfilling was not performed in accordance with the regulations, the Site Supervision can ask for the excavation and backfilling on the poor quality compacted areas to be repeated.

10.3.6	The construction of sand bed (item N 3)

Prior to placing of pipes, the trench bottom must be covered with 8mm grain sized sand in at least 10cm thickness. The sand must be equally spread in a continuous longitudinal fall so to follow the pipe path.

The first layer of sand will be somewhat thinner in the middle where some 30 cm of the pipe width will be placed so that the pipe is equally covered which implies that the bed would be at least 2cm higher on the sides of the pipe.

After pipe has been placed the sand bed would be manually compacted so that the pipe rests on equally thick sand layers.

10.3.7	The construction of gravel base under the structure (item N 4)

The thickness of the gravel base would be as shown on drawings.

Natural unscreened material size which can be used for gravel base cannot exceed ½ of the requested layer thickness, i.e. not more then 10cm in radius. As a replacement, broken stone conforming to the same criteria can be used, or if approved, screened clean stone material from the excavation. If the material from the excavation is going to be used, all pieces and grains larger then ½ of the layer thickness, i.e. not more then 10cm in radius, must be removed.

Aggregate or stone material to be used can not contain any impurities, organic residuals, topsoil and not more then 10% of particles that can pass through a 0.09mm sieve. In case of crushed stone material or natural aggregate, the use of soft breccias, slates, marlstones and similar materials will not be allowed. The material must be of a sound non-dispersed lime, dolomite or rock of a similar quality.

If the possibility of an underground or any other water to emerge does exist, gravel layer must be such to enable the water to outflow and prevent fresh concrete scour.

10.3.8	The construction of vertical gravel drainage system around the structure

Vertical gravel drainage of gravel embankment around all partly covered structures will be performed in thickness as shown on drawings.

The material to be used for the construction of vertical gravel drainage could be unscreened gravel of a maximum grain size of 3cm.

The gravel must not contain impurities, organic material in the topsoil and clay particles. There cannot be more then 10% of particles that can pass through 0.09mm sieve.

The border between the vertical gravel drainage and embankment material must be such to disable the interaction of the two materials.

The vertical gravel drainage is performed around drainage pipes whose position must not be disturbed by these works.

10.3.9	Measurement and payment

The material quantities that are to be calculated for the payment are the ones of the materials used in accordance with the Technical Terms as described in this chapter.

Items:

N 1 Dredging of sand

N 2 Backfilling of foundations and trenches after executed works

N 3 The construction of sand bed

N 4 The construction of gravel base under the structure

N 5 The construction of vertical gravel drainage system around the structure

will be paid per cubic meter of the used material as per drawings and as determined by the Site Supervision.

11. MASONRY WORKS

11.1. BRICKWORK

11.1.1	General provisions

Masonry material must be of a good quality, and the construction must be professional and in accordance with technical standards and regulations.

The following brick types will be used for the brickwork:

- Solid clay brick – JUS B.D.011

- Solid clay facing brick – JUS B.D1.013

- Hollow clay brick - JUS B.D1.015

- Voided clay slabs - JUS B.D1.022

- Sand lime blocks and bricks

Brick quality will be tested in accordance with JUS B.D8.011 standard.

The mortar used in the brickwork will be in accordance with JUS U.M2.010 standard and its quality will be tested in accordance with JUS U.M8.002 standard.

Cement and water to be used for mortar preparation must be of the same quality as the one used for concrete, as described by these Terms in the chapter on concrete.

Lime to be used for mortar preparation must be in accordance with JUS B.C1.020 standard and its quality will be tested in accordance with JUS B.C8.040 and JUS B.C8.042 standards.

Brickwork is to be executed as per plan, in regular bonds and horizontal lines without the use of the pieces smaller than ¼ of the brick. Small pieces must not be placed next to each other in the wall.

Joints must be completely filled with mortar whose thickness cannot be less then 1cm.

1.5 – 2 cm less mortar is to be used on external joints for better connection with plaster later on. The excess mortar is to be removed by trowel while still fresh.

For partition walls made of half a brick, in each fourth row of a bearing wall, half a brick is to be left sticking out. For partition walls of 6.5cm, ¼ of the brick is to be left out to form chase in the bearing wall throughout its height.

Six pieces of trapezium pallets of 5 x 8 cm in size with “tails” for door placing are to be anticipated. They are included in the cost of brickwork. Pallets must be covered in carbolineum for the protection from moist.

In case the brickwork is stopped due to cold weather, all walls must be covered and protected from water and frost using board shuttering along the walls. In case the walls are damaged due to improper protection, the damaged areas must be demolished and rebuilt which will not be compensated for by the Employer.

The mortar can be made only in the quantity that can be built in before it starts setting. The required consistency must be maintained. Hardened mortar cannot be used. The preparation of mortar must be in accordance with standards and ratio as described in the Bill of Quantity item.

Openings in walls, such as window panes and similar, will not be paid separately because they are calculated in cubic meters for the brickwork as a whole, and unit rates show the cost of the work and material required. The costs of construction of all openings, chases for vertical sewage conduits, electrical conduits, downspouts and similar will not be paid additionally and will be included in the unit rate for brickwork. Likewise, the later covering of installations, their plastering and scrimming will not be paid additionally and will also be included in the unit rate for brickwork.

Openings for doors, windows and partitions as well as lintel beams are deducted from the total volume of brickwork, where as window dentils are included in accordance with measures described in the plan. Decrease of wall thickness at wall openings, if any, will not be deducted from the volume of brickwork.

11.1.2	Facing brickwork of 25cm in thickness using facing bricks without front side plastering

Attention is to be paid to ensure that the bond is regular and therefore pieces smaller than half of a brick or block cannot be used in the brickwork. Horizontal and vertical joints must be of an identical width throughout and the mortar must be thinner for at least 2cm than the outer brick line.

The special attention is to be paid that the mortar does not leak anywhere and that no brick in the wall is sprinkled by it.

Bricks and/or blocks used for this type of brickwork must be of the same color without traces of saltpetre, with perfectly sharp edges and must be frost resistant.

Unit rate for brickwork also includes pointing by mortar in 1:3 ratio.

The payment will be performed by cubic meter of brickwork.

11.1.3	Payment

The payment will be performed by unit rates for square or cubic meter as offered in the Bill of Quantities for brickwork. The offered unit rates include the costs of works, materials, scaffolding and all other costs of brickwork.

Bond beams in partition walls will not be paid separately and their cost should be included in the offered unit rate.

11.2. PLASTERING

11.2.1	General provisions

The plastering is to be performed when the building is relatively settled and wall completely dry. The air temperature during plastering is performed must be suitable.

The plaster must be in accordance with JUS U. M2.012 standard, and its quality will be tested as required by JUS U.M8.002. standard.

Cement and water must be of the same quality as for concrete preparation.

Lime used for plaster preparation must be in accordance with JUS. B.C1.020 standard and its quality will be tested in accordance with JUS. B.C8.040 and JUS. B.C8.042 standards. Plaster preparation must be in accordance with regulations and the ratio of components as required by the item description from the Bill of Quantities.

The walls must be clean and dry before plastering, i.e. wetted as required, especially when plastering using cement mortar. Joints are to be cleaned from the excess mortar on a depth of 1.5cm for better connection with plaster.

In case the saltpetre appears on walls, it is necessary to remove it using the brush and clean the walls using hydrochloride acid diluted in water in 1:10 ratio.

All concrete surfaces must previously be sprinkled by lean cement mortar which is included in the unit price and is not paid separately.

Plastering is to be applied in two layers in total thickness of 2cm – 2.5 cm in the following manner: the first layer is to consist of plaster containing rough, screened sand, and the second layer will contain fine sand and will be applied only after the first layer is properly dried. The edges must be slightly rounded, and ceiling corners sharp and at the right angle.

The scaffold must be self-supporting and equipped with manual or mechanical winch, platform and safety rails. The approval for the use of scaffold will be issued by the Site Supervision.

11.2.2	Payment

The payment will be performed as per unit rates for square meter. The costs of all works and materials, mantling and dismantling of scaffolding inside and outside, covering installation, window and door cleaning and any other costs caused by plastering will be included in the unit rate.

11.3. FAÇADE WORK (JUS U.F2.010)

Façade work implies veneered construction using noble and plastic plaster and façade paints for the protection from precipitation, as a heat and a sound insulation and for the precipitation sediment and diffuse steam conduction.

The materials to be used must be in accordance with appropriate JUS standards and technical terms from this standard.

The materials for which there is no JUS standard must have quality certificate confirming the suitability for the particular use.

In case the technical description does not describe any particular material, the Contractor obligation is to choose and prepare the material in accordance with the base layer, required construction procedures and conditions of the base at the time of the works.

Materials are to be used only on surfaces for which their physical, chemical and mechanical properties are suitable.

For plaster preparation for the base layer and artificial stone, the cement quality given in JUS B.C1.01 standard is to be used.

Clean mineral aggregate (sand and gravel) of the proper grain size is to be used for the construction of the base layer. The largest grain size cannot exceed 8mm.

The paints of the organic or non-organic origin must be constant in the binder that is going to be used and light and precipitation resistant. They also must be nicely ground and of a same grain size.

Water must be clear (in accordance with technical terms and requirements for concrete and reinforced concrete), no chemical or other residues which would have an unfavorable effect.

Plastic plasters are final industrial products whose main ingredient is synthetic resin that enables good adhesion to the base, elasticity and fast drying.

Those paints also contain fillers – stone aggregates of various colors and grain sizes, tints and water.

Plastic plasters must be resistant to precipitation, light, frost and fire. The tint must be constant, water resistant, water proof and easy to apply.

11.3.1	Waterproofing agents

Waterproofing agents are used to enable adhesion of the plastic plaster to the base and to decrease base absorption and therefore they must have good impregnating properties.

11.3.2	Façade paints with solvents

The paints must be resistant to precipitation, light and all chemical influences from the atmosphere.

The thinners used on paints with solvents, as well as waterproofing agents, must be industrially produced and can be used in quantities as specified by the manufacturer.

Dispersion paint must be resistant to washing, corrosion and precipitation. They are applicable to various base types previously treated with dispersion putty.

The putty must be of a constant volume, cannot start peeling off and must be properly bound to the base.

The surface that is to be covered by any type of decorative plaster must be sufficiently rough, stabile and cleaned from grease, lime paint, gypsum and any other impurities.

Discrepancies from the designed position cannot be more than allowed 2 cm per 10 m.

Base layer must be properly bound to plaster surfaces and must be sufficiently compact for applying the upper – finishing layer. The surfaces that are to be worked on must be prepared so that the base layer can be bound properly. The preparation principle depends on the material type the construction is made of.

In case of a concrete base, the roughening must be performed by chiseling, then wetting and spraying with lean cement mortar using screened gravel in 1:2 ratio.

Cement mortar of 2cm in thickness is applied to a surface prepared like that and serves as a base layer for artificial stone, or compo of 2cm in thickness is applied as a base for noble plaster.

The surface of the base layer must be rough so that the finishing layer can be bound better.

The base layer must be flattened by clear small grain sized sand – in case plastic mortars, dispersion paints and paints with solvents are used as a finishing layer.

Putty is used as a leveling course on concrete surfaces that will serve as a base for plastic mortars. Before the putty is applied, concrete surfaces must be cleaned from dust and material residuals (concrete, mortar and other). Putty is applied by broad knife in the layer thickness of 1mm to 2mm.

12. CONCRETE WORKS

12.1 General

12.1.1	General provisions

All concrete works will be performed as shown on working drawings or on ones required and approved by the Site Supervision. If the Contractor suggests any change in the construction, he is under obligation to submit the suggestion along with proofs on stress and deformation to the Site Supervision for approval at least thirty (30) days prior to the construction of the section in question.

12.1.2	Regulations and standards

The Contractor is under obligation not only to follow these Technical Terms when executing all concrete work phases, but also to follow the current rules and regulations as well as all standards directly and indirectly referring to concrete works.

12.1.3	Concrete composition

The concrete consists of cement, small and large grain sized aggregate, water and additives that create voids in fresh concrete if they are proven by preliminary testing to improve certain concrete properties and at the same time do not have any negative influences to other components, or to concrete itself or the reinforcement or any other built in element.

All materials that are going to be used in concrete preparation must be in accordance with these Technical Terms and current rules and regulations.

12.1.4	Preliminary and control testing of concrete and its components

The Contractor’s obligation is to perform preliminary and control testing of concrete and its components supervised by the Site Supervision and in accordance with these Technical Terms.

All testing will be performed by the accredited laboratory hired by the Contractor for those purposes.

All the expenses for preliminary and control testing will not be additionally paid to the Contractor but will be calculated in the unit rate for concrete.

The Contractor is under obligation to allow the Site Supervision to take the samples of concrete and its components for control testing during the construction for the purposes of quality proving as well as samples that will be tested later on.

In cases when control testing show the fresh concrete and its components do not conform to the required quality, the Contractor is under obligation to take the necessary measures so to improve the quality during the procedure in order to reach the required one. The quality will then be proved by additional control testing. If the Contractor fails to reach the required quality after performing the remedial measures, or the Site Supervision considers it insufficient, the concreting will be stopped and the Site Supervision is the one to reach the decision on how the works will be stopped as well as on remedial measures that are going to be applied (removal of concrete, possible rehabilitation and similar).

If concrete cube control testing, or any other control testing performed after a certain period of time, do not show the required results for the built in concrete, the Contractor’s obligation is to take out the samples from the areas determined by the Site Supervision and submit them to the Site Supervision for further testing. The testing of these samples will be performed by a specialized organization listed in these Terms under the control of the Site Supervision. In case this testing fails too, the Site Supervision will determine on further steps to be undertaken (removal of concrete, possible rehabilitation and similar).

All additional works on rehabilitation, removal, repeated concreting and similar, as required by the Site Supervision after the results of all control and repeated testing proved negative, are to be undertaken by the Contractor at his own expense. The Contractor will also have no right to claim for time extension based on the delays caused by additional works of this type.

The costs of all control testing that give negative results will be covered by the Contractor.

12.1.5	Concrete laboratory

The Contractor must have the site laboratory for the testing of concrete and its components.

Site laboratory must be equipped for the testing that is going to be performed on site.

The laboratory will keep the precise record on all samples and performed tests.

The laboratory will also keep the record on all preliminary and control testing performed at the accredited laboratory. The record will be submitted to the Site Supervision for inspection in the form he requires.

The Site Supervision will also supervise the laboratory and its employees.

The costs of laboratory construction, furnishing, work and removal after works have been finished would not be paid separately.

12.1.6	Concrete work diary

From the beginning until the end, the Contractor is to keep the diary of concrete works. The diary must contain all data concerning the complete process of concreting and conditions under which it was performed. The structure and the block that is being concreted must be stated in the diary, as well as the beginning and the end of concreting, type of concrete, cement, aggregate and additive origin and quality, mix components and cement quantity, water-cement factor, also the preparation, transport and built in procedures including the information on thickness and number of layers. All changes in these data, if any during the concreting procedure, any possible delays and causes and duration of the same and any other significant events that could influence the procedure need to be recorded in the diary also. The diary must also contain the record on weather conditions: the temperature and air humidity at the beginning and at the end of concreting, i.e. every six (6) hours if the concreting lasts for a longer period of time, as well as data on performed control testing and taken samples and any other data required by the Site Supervision.

12.1.7	Concrete work and concreting programme

The Contractor is to prepare the appropriate Programme of Works in accordance with the Terms of Contract. It would also include the programme of concrete works.

When preparing the programme i.e. Formwork Design, the Contractor must pay attention to time required for the works to be performed and when finished, the programme is to be submitted to the Site Supervision on time.

The Contractor would not have the right to claim for time extension if the delay in concreting was caused by untimely submittal of the programme, or in case when the Site Supervision for some reason did not approve the programme in question but rather returned it to the Contractor for additional changes.

The Contractor must coordinate the works of all participants in the construction when preparing the programme.

12.1.8	The approval for concreting

The Contractor cannot start with any works on concreting before obtaining the approval from Site Supervision noted in the construction diary and the required form. This refers to all the elements of concrete and reinforcement works: foundation and working joints, shuttering, scaffolding, and reinforcement, all items that are built into the concrete including aggregates and cement as well as equipment for transport and concreting.

Control and approval for concreting will be given partially for individual elements by the Site Supervision, but the concreting itself cannot start before all block elements are approved. The Contractor will not have the right to claim any additional costs for: not submitting the request for concreting on time, duration of the control and postponement of the approval and additional control in the aforementioned situation.

12.2 CEMENT

12.2.1	Cement quality

Portland cement 15Z PC 35 for hydro-technical constructions with the strength of 35 KN/cm after 28 days will be used in all concrete works.

If there is a requirement for the use of any special cement types during the construction, the change must be approved by the Site Supervision.

12.2.2	Transport and storing of cement

Cement will be taken to site in bulk by special vehicle. Once on site, the Contractor will undertake all measures required to keep it protected from humidity. When reaching the site, the cement temperature cannot be higher than 60°C.

Cement will be stored on site in dry and properly ventilated storage rooms (silos). Silos must be constructed so to provide the protection from bad weather conditions. Prior to mantling, the Contractor is under obligation to obtain the approval on the silo construction from the Site Supervision. Silo capacity is to be dimensioned in accordance with the requirements from Special Terms.

For minor concrete works, the Site Supervision can approve the use of cement in bags. Its storage must be under the cement shed. Cement storage directly on the soil is strictly forbidden.

The Contractor will pay the special care to the cement that must be kept completely dry.

In case the cement coagulated while stored, in can be used only if the particles can be crashed by slightly pressuring them with fingers. If that is not the case, its use will not be allowed for the construction.

When storing the cement, the Contractor must keep the record on the manufacturer and cement type, date of its production, means of transport, date it reached the site and on place and way it is stored. The Contractor must also inform the Site Supervision on each cement load reaching the site, and submit all the records if required.

The Contractor will keep the record on all data on cement supplies and its usage in the concrete construction diary.

The Contractor will keep track that the cement is used in order it reached the site. The use of cement before it is matured is not allowed. Before concreting of a block starts, the Contractor must give evidence to the Site Supervision he has at least 20% more cement stored than it is necessary for concreting.

12.2.3	Preliminary cement testing

Preliminary cement testing must prove the cement has a required strength, the beginning and the end of setting and soundness of cement in accordance with JUS B.C8.022 and JUS B.C8.023 standards.

The Contractor must check whether the manufacturer’s declaration conforms to the quality required by the JUS B.C1.011 standard.

If the Contractor suggests for any reason the change of cement (different manufacturer, cement composition and similar), he must submit cement samples to the Site Supervision for testing.

12.2.4	Control cement testing

The Contractor’s obligation is to perform cement control testing during the concrete works in the way required by these Technical Terms.

Control testing will be performed on daily basis during the ongoing concrete works, and cement will be tested to secondary consistency, setting time and soundness of cement. Testing will be performed in accordance with JUS B.C8.023 standard.

If control testing show nonconformity to some of the quality requirements, the use of such cement will be stopped until the certificate of compliance is obtained.

12.2.5	Payment

The costs of supply, transport and storage of cement will be calculated in the unit rate for concreting and will not be additionally paid for.

12.3	AGGREGATE

12.3.1	Aggregate quality

Aggregates to be used in concrete preparation are the ones in accordance with the quality requirements determined by BAB rulebook and JUS B.B3.100 standard. Those requirements refer to petrographic and mineral composition, grain shape and quality, strength, frost resistance, content of organic matter, sulfates and sulfides and small particles.

12.3.2	Aggregate fractions

Aggregate to be used in concrete must be divided and proportioned in fractions. Concrete type 30 made of natural aggregate mix is not allowed. Aggregates will be divided into five fractions in the following manner:

- for small grain size aggregate: 0.1 – 1 mm; 1 – 4 mm; 4 – 8 mm

- for large grain size aggregate: 8 -16 mm; 16 – 32 mm.

Optimum grain size distribution will be experimentally determined in preliminary testing.

The Contractor can change the grain size distribution of the aggregate mix only based on new proves and additional preliminary testing approved by the Site Supervision.

When preparing the Programme of Works, the Contractor must take into account all the quantities of required aggregate and it is his responsibility to provide them in a timely manner. Aggregates must conform to valid rules and regulations both in quality and composition. As a part of Programme of works, the Contractor will prepare the plan and also obtain all approvals and permits for aggregate exploitation.

12.3.3	Preliminary aggregate testing

Aggregate quality, possible quantities for exploitation and grain size distribution are to be determined by preliminary aggregate testing.

12.3.4	Control aggregate testing

Control testing will be performed continuously throughout the works so that the conformity to the quality required by BAB rulebook is confirmed. The testing will also be conducted to confirm the material composition is not different from the one determined by preliminary testing or at least not in the manner to have an influence to concrete quality.

The quantity of fine particles in a small grain size aggregate will be tested daily in accordance with JUS B.B8.036 standard. Humidity of aggregate fractions will be tested at least once in eight hours, and if required (supply of new aggregate, in case of rainfall or increased evaporation) even more often in accordance with JUS B.B8.035 standard. The correction of water quantity added at the concrete plant will be performed based on the obtained results.

Grain size distribution will be tested once a day analyzing fresh concrete components. In case these results show the discrepancy with the required grain size distribution, the Contractor must check each fraction on a larger number of sieves in accordance with JUS B.B8.029 standard.

Control testing of petrographic and mineral composition and chemical components will be performed at least once in three (3) months, or more often if the Site Supervision required it because of the changes noted in aggregate composition.

In case the control testing show that material properties do not conform to required standards, the Contractor will make proper corrections.

12.4 	WATER

12.4.1	Water quality

The water to be used in concrete preparation is the one determined by preliminary testing not to have unfavorable effects to the concrete, i.e. that the water properties conform to JUS U.M1.058 standard.

The water used for concrete curing must not cause any damage in contact with concrete surface, i.e. that its properties conform to BAB rulebook when it comes to sulfates and organic matter content.

12.5	CONCRETE ADDITIVES

12.5.1	General provisions

Used additives must conform to JUS U.M1.035 standard. Before additives are used in concrete preparation, it must be checked whether it is suitable for the designed concrete mix in accordance with JUS U.M1.037 standard.

12.5.2	Mandatory concrete additives

All concretes must be provided with voids in fresh concrete unless the Site Supervision instructs otherwise. Voids are provided by adding a certain additive that would conform to JUS U.M1.034 standard during mixing procedure. This additive will be added to fresh concrete so that the content of voids is not less than 3.5% and not more than 6% of the total concrete volume.

12.5.3	Optional concrete additives

The use of other tape of additives is allowed if the Contractor proves their necessity for achieving the fluidity of fresh concrete or for regulating the time required for cement binding. The Contractor must also submit the proof on preliminary concrete testing and certificates of compliance which show the use of this type of additives will not weaken the basic properties of concrete and reinforcement. Their use must also be approved by the Site Supervision.

12.5.4	Testing of concrete additive properties

The Contractor will not perform the testing of additives but must provide the appropriate certificates of compliance from manufacturers for each new supply show them to the Site Supervision and keep them as a part of the technical documentation used later on for proving the quality of executed works.

The Contractor must store and use additives as per manufacturers’ manual. No use of additives without the certificate of compliance or after the expiry date is allowed.

If the Site Supervision requires, due to improper storage, the Contractor must perform control testing of additives which could have changed their properties, even though the expiry date is still valid.

The costs of these testing will not be additionally paid for.

All other testing of concrete additives are performed when preliminary and control testing of concrete itself are conducted.

12.5.5	Payment

Supply, transport, storage and other costs for concrete additives will be calculated in the unit rate for built in concrete and will not be additionally paid for.

12.6. CONCRETE

12.6.1	Concrete type and quality

Concrete type and quality are defined on drawings of certain structures and in work item descriptions.

The properties of concrete types to be used in this Contract are the following:

- Hydro-technical concrete of type CG 30, impermeability V-8 and frost resistance M-100 for the constructions in touch with water

- Concrete of type CG 30 used for the constructions where impermeability is not required

- Concrete of type CG 15 used for filling and leveling layer

The maximum grain size aggregate of 32 mm will be used for all concrete types.

12.6.2	Preliminary concrete testing

Optimum concrete mix, including grain size distribution, will be determined by preliminary testing. In case preliminary testing show those other additives are also required, the optimum quantity of them will also be determined.

The Site Supervision will determine the terms of fresh concrete consistency based on preliminary testing results either at the batching plant or at the place of built in. The consistency will be checked using the Slump test.

12.6.3	Control concrete testing

Control testing will be performed in order to show the properties of concrete mix, transport and built in concrete are as required. In cases the required properties are not achieved, the Contractor is under obligation to perform all the works, at his own expense, necessary to achieve the required concrete quality. Those will include improving the concrete components, means of preparation, transport and built in as well as the rehabilitation of hardened concrete and even, if required by the Site Supervision, its removal and replacement.

At least once a week, and if required by the Site Supervision more often, a sample from the mixer must be taken and the mix tested so that the degree of density, the grain size distribution of the aggregate and water and cement quantity in concrete can be determined.

Fresh concrete consistency (slump) will be controlled every two hours at least as is in accordance with JUS U.MB.050 standard.

The quantity of voids in fresh concrete is measured at least once within 8 hours in accordance with JUS U.M1.031 standard.

Fresh concrete temperature is measured at least once in 8 hours once taken out from the mixer. If air temperatures are below -5°C and above 25°C concrete temperature must be measured every 2 hours.

Maximum concrete temperature at the time of placing must not be more than 30°C or less than 5°C.

The control of concrete mix transport consists of checking the density, consistency and temperature of the mix, in time intervals determined by the Site Supervision, and compared with the preliminary testing results and approved way of transport.

The control of built in concrete is performed by comparing the hardened concrete in laboratory conditions with the one at the place of construction.

Quality control of the concrete that is being produced is performed by determining its compressive strength in accordance with JUS U.M1.020 standard, bending strength in accordance with JUS U.M1.010, impermeability in accordance with JUS U.M1.015 and frost resistance in accordance with JUS U.M1.016 for parts of structure for which it is required. Bulk density must also be determined, as well as all other testing, by measuring the samples.

For testing the compressive strength, the number of samples must be at least three on each 500 m of built in concrete. If more concrete types are used at the site, the number of samples must be determined in accordance with the aforementioned demands. The Site Supervision can require testing of samples before or after 28 days.

For testing the bending strength, the number of samples must be at least three on each 500 - 700 m of built in concrete.

For testing impermeability of concrete it is necessary to perform at least one series of tests on 6 samples on each 500m of built in concrete.

The Site Supervision will additionally determine the parts of the structure and time interval in which frost resistance tests will be performed. Test results on compressive and bending strength must be statistically processed following the required criteria for quality.

In case some samples do not show the required quality, the Site Supervision can ask for cores of 15cm in radius to be taken out and tested in the laboratory he chose. In case the laboratory and/or additional testing show the quality of samples not to be the required one, the Site Supervision will decide on further steps to be undertaken. The costs of these testing will be covered by the Contractor.

12.7. CONCRETE PREPARATION

12.7.1	General provisions

The Contractor’s obligation is provide and maintain the batching plant that will produce the concrete of a required quality and which will be of a sufficient capacity so to be in accordance with the programme of works. The Design for the batching plant, the Contractor will submit for approval along with Tender as a preliminary solution for the programme of works.

Only the use of automatic batching plant is allowed.

12.7.2	Concrete mixing

Mixing time is to be experimentally determined, paying attention that optimum density is achieved. The discrepancy from the required quality allowed is that difference in cement - sand and water-cement factor ratio is less than 10% between fresh concrete samples taken from front, back and the middle of the mixer ad the ones taken at the beginning, in the middle or at the end of concrete pouring from the mixer.

12.8 TRANSPORT OF CONCRETE

12.8.1	General provisions

Transport here implies the transport of concrete from the batching plant to a place where it is unloaded and from there to a place it is built in.

12.8.2	Transport from batching plant to structure

Transport from batching plant to structure must be performed in the fastest possible manner, so that segregation, component losses, temperature increase and water losses are prevented.

12.8.3	Transport from a place where it is unloaded to a place it is built in

Transport from a place where it is unloaded to a place it is built in must be performed in a way to prevent segregation and component losses.

The use of inclined ramps is not allowed unless their length is less than 3.0m of the 1:2 slope, to which the concrete is directly poured and directly built in.

Free fall of concrete is not allowed. On places where free fall is inevitable, the contractor will use a tremie previously approved by the Site Supervision.

The start and the end of built in must be performed in the following time intervals counting from the time concrete is poured from the mixer.

| Mix temperature in °C | Maximum interval between mixing and start of built in | Maximum interval between mixing and end of built in |
| --- | --- | --- |
| 5 - 10 | 1h 30 min | 3 h |
| 10 – 15 | 1h 15 min | 2 h 30 min |
| 15 - 20 | 45 min | 2 h 15 min |

For concrete mix temperatures between 20°C and 30°C, the intervals will be determined by the Site Supervision.

In case the cement which starts binding before 1h and 30 min is used, the above given values are not applicable and the Site Supervision will issue new ones.

Time intervals from the table above can be prolonged for the duration of transport in case light mixing is performed, only if time interval does not exceed 60 minutes.

When air temperatures are high or low (above 30°C and below 5°C), concrete mix must be properly protected during transport.

12.8.4	Concrete pumping

The decision on concrete transport by pumping is made by the Site Supervision after consulting the Designer when approving Concrete Design. Transport of concrete by pumping is not allowed for crane paths, bridge, floor and roof constructions.

The Contractor must provide all required concrete properties both for the concrete that is partly and the one that is wholly transported by pumping. The properties are proved by control testing.

12.9. SURFACE PREPARATION FOR CONCRETING

12.9.1	General provisions

Concreting is performed: on previously excavated surfaces (whether or not the excavation is protected), on already concrete surfaces, on properly shuttered surfaces, and on surfaces where hydro-mechanic, mechanic and other equipment is going to be placed.

Term “surfaces” implies all surfaces that are being freshly concreted regardless to the angle with horizontal.

The Contractor must prepare all surfaces for concreting in accordance with these Technical Terms, and the Site Supervision will afterwards perform the check and give the approval for concreting.

12.9.2	Preparation of foundation joint

Foundation joint implies all contact surfaces between concrete and soil, i.e. surfaces of the excavation where concreting is performed, regardless to the shape and slope. The Contractor must properly secure the foundation joint from underground waters for which he requires the approval from the Site Supervision. Concrete type 15 and in thickness of 10cm will be laid as a leveling course. After this layer is stiffened, waterproofing, if any, can be laid and then the reinforcement.

12.10 CONCRETING

12.10.1	General provisions

The Contractor will prepare the Programme of concreting which will show the position of blocks, concreting phases and concreting dates and submit it to the Site Supervision for approval.

12.10.2	Concreting

Prior to concreting, the Contractor will submit to the Site Supervision a standardized form showing that the following are ready for works: shuttering, support, reinforcement and permanent elements. It will also show that surfaces are ready for concreting as well as batching plant, transport vehicles and the equipment for concrete built in and curing.

Concreting will be performed in accordance with the design approved by the Employer.

Concreting will start only after the Site Supervision issues a written approval for each individual block.

Concreting will not be approved if the Site Supervision thinks the weather conditions are not favorable.

12.10.3	Concrete vibration

Concrete will only be compacted mechanically.

Vibration equipment of at least 6000 cycles per minute will be used. The type of equipment must be in accordance with concrete type, aggregate grain size, block dimensions and layer thickness. During the process of compaction, the vibrating needle must reach into the previous layer at least for about 5cm. The compaction is performed up to the point the cement slurry appears on the surface. The special attention is to be paid to concreting around all built in elements, gaskets and along the shuttering.

Certain layer thicknesses will be determined by the Design, batching plant capacity and block dimensions. Minimal layer thickness is 20 cm and maximum is 50 cm.

Concreting around installation will be performed with caution and in thinner, even layers so that no installation is damaged.

12.10.4	Brakes in concreting

Concreting will be performed as a continuous work.

In case of force majeure the Contractor has to stop concreting before finishing, he will then continue after forming a horizontal joint or use some other solution as required by the Site Supervision.

Before the works continue, the joint must be processed as described in item 12.11.

12.11. CONCRETE JOINTS

12.11.1	General provisions

Term “concrete joints” in these Technical Terms refers to all joints between already stiffened and fresh concrete forming thus one whole.

Two types of joints are distinguished here: free joints (horizontal, or under a slight angle where the surface of previously concreted element is free and easily approached) and joins with shuttering – vertical and steep surfaces formed by placing the shuttering.

12.11.2	Joint processing

Prior to concreting, all joints must be properly roughened, cleaned and exhausted. Roughening will be performed by removing cement film from the joint surface. The removal of cement film on free surfaces will be performed by washing, using water and air mixture under pressure of at least 5 bars. The surfaces with shuttering are processed by manual chiseling or using pick hammers.

When it comes to free surface roughening, the Site Supervision will determine the best time for those works depending on season and the efficiency of the procedure itself, paying attention that the procedure does not remove large grains from the concrete surface. In case the Contractor does not perform roughening by washing, he is under obligation to do it by chiseling. In that case, pick hammers cannot be used before 24 hours after concrete binding have passed.

Before concreting works are continued, the Site Supervision will check and approve concrete joints. The old concrete will be sufficiently wetted so it does not draw in the moist from the fresh concrete.

When preparing the concrete design, the Contractor will pay attention not to create concrete “pits” in work blocks which would be hard to clean and prevent washing and exhaustion. In case the Contractor does suggest such a way of construction, he must anticipate the construction of appropriate openings or pipes in the level of “pit” bottom and thus provide the cleaning of joints. Those openings or pipes will be properly sealed, as approved by the Site Supervision, after concreting has been finished.

12.12. CONCRETE EXPANSION JOINTS

12.12.1		General provisions

The term “expansion joints” refers to the contact between two concrete surfaces where no firm connection is formed but rather free movement up to a certain point is allowed.

12.12.2	Expansion joint types

Expansion joints can with gaskets that prevent water or injection mass to go through, or without gaskets.

They can also be vertical, horizontal or skewed.

Forming of contact areas on all expansion joints, with or without gaskets, is part of concrete works.

Shape and dimensions of expansions joints must be as given in drawings, i.e. as required and/or approved by the Site Supervision.

12.12.3	Sealing material

Sealing of expansion joints is performed by placing PVC, rubber or sheet copper tapes, or their placing in the concrete of neighboring blocks/construction parts.

12.12.4	Sealing tapes

For the purposes of continuous joint sealing, PVC or rubber tapes approved by the Site Supervision are placed.

Sealing tapes must be supplied to construction site in large wheels to minimize the number of joint extensions. Before supplying the tape, the Contractor will bring the sample and manufacturer’s certificate of compliance to the Site Supervision for approval. The materials used for sealing tapes must have the ultimate strength of 6 to 7 KN/cm and 200 or 300 percent of elongation. If the Site Supervision deems it necessary, he can order laboratory testing of the sealing tape. The costs of possible control testing are considered included in the unit rate.

All sealing tapes must be placed in such a way that the part of the tape concreting in a block must be at the right angle with the joint and the flush. The tape must be held in such a position during the concreting so that it does not bend. Special attention is to be paid when concreting the tapes along horizontal joints. In such cases, the Site Supervision can require concreting to be performed manually.

Extension of expansion joints will be performed solely by welding.

All tape crossing will be made by appropriate purpose made pieces.

12.12.5	Payment

The payment will be performed by unit rates for a meter of sealing tape. The unit rate is for all works, material, equipment and other costs regarding supply, transport, storage, placing and all extensions of sealing tapes, also including possible control testing.

12.13 FALSEWORK

12.13.1	General provisions

The Contractor will place the appropriate falsework where necessary and thus form the concrete in dimensions shown on drawings and provide its forming until it is hardened.

The following shuttering types are distinguished:

OR 1 Rough shuttering – in accordance with terms 12.19

OR 2 Regular shuttering - in accordance with terms12.19

OR 3 Special shuttering - in accordance with terms 12.19

Note: Shuttering placed between joints of certain blocks is not specified. Its price is included in the concrete price. Surfaces of various niches and openings where shuttering is concreted in and covered by secondary concrete are also counted as joints.

12.13.2	Falsework material

Falsework material is not specified and the use of various materials is allowed such as: wood, sheetmetal, steel constructions, masonite and similar materials prefabricated from wood. All materials must be in accordance with the quality and bearing requirements. The use of steel shuttering is obligatory for precast elements.

12.13.4	Falsework Design

The Contractor must submit the Falsework Design, which would be the part of the Concrete Design, to the Site Supervision for approval.

The Falsework Design must show stability and bearing capacity of falsework for all construction phases. Stress must be within the allowed limits for the materials used for falsework. Bearing capacity must be calculated for all elements that will suffer the pressure of fresh concrete. Falsework deformation must be calculated for all elements, and the Design must show appropriate precambers.

In case formwork is used on existing constructions and structures, the bearing capacity for that type of load must also be proven.

Falsework design must also take into account the bearing capacity of the complete stress of concrete itself and pay load that can occur. In case of phase concreting, the Contractor can calculate the stress of the following phase when constructing the previous one if the way of construction is as per the Final Design and does not endanger the stability of the previous phase or the structure as a whole.

In case such a construction is approved as per Contractor’s requirement, and additional reinforcement is required for achieving the stability, it will be paid by the Contractor without the right to claim.

Regardless to the fact the Design is approved, the Contractor bares the sole responsibility for proper placing, stability and safety of falsework.

12.13.5	Construction, mantling and dismantling of falsework

The Contractor must use, where possible, patent falsework. Cutting the shuttering in situ will be allowed only if necessary. The shuttering must be impermeable to prevent leaking of cement mortar. The gap between shuttering elements must not be more than 1mm or 2 mm. All anchors that hold the shuttering for the following phase must be placed sufficiently from the edge of the concrete not to cause concrete damage.

Cutting, mantling and dismantling of shuttering can be performed by specialized personnel only. The Contractor must undertake safety measures for working on heights, and the approach to falsework must be secured for cleaning and control.

Shuttering surface must be clean from hardened concrete residuals and engine oil, or similar, must be applied to it for easier removal. All wooden surfaces of shuttering will be wetted by water to prevent the loss of moist from fresh concrete.

Side shuttering will be removed only when concrete reaches the strength of 3.0 KN/cm, which is determined by preliminary testing.

Horizontal, bearing shuttering will be removed after the period given by the Design has passed, i.e. when the stability and bearing capacity of all concrete phases has been proven. The decision on the removal of this shuttering is reached by the Site Supervision.

12.14 CONCRETED ITEMS

12.14.1	General provisions

Concreted items are the ones concreted partly or fully in fresh concrete as per designs and the Site Supervision instructions. This also refers to all elements placed in already concreted niches that are later on concreted in by the secondary concrete layer.

These provisions do not refer to items separately specified, such as reinforcement, water pipes, sewage and other installations as well as steel support.

Anchors and similar elements, built in for Contractor’s purposes of securing shuttering, reinforcement, scaffold holders, equipment and any other work purposes, are not considered to be part of concreted items.

12.14.2	Delivery of concreted items

All concreted items can be the ones delivered by the Contractor or any other participants in the construction.

Specification of items, delivered by the Contractor, will be additionally determined by the Final and Construction Designs.

All used items must be of a required material in accordance with marking on drawings.

Record will be made by the Contractor in the presence of the Site Supervision on concreted parts delivered to the site by other participants. Time, place and means of taking over will be determined by the Site Supervision for each case separately. The only responsible for items after taking over is the Contractor and is under obligation to store them and used them properly. All costs of possible damages due to improper storing after taking over will be covered by the Contractor.

The Contractor is not responsible for the quality of concreted items delivered by other participants if it is evident that he treated them and built them in properly.

All specified items the Contractor procured on the market, as ordered by the Site Supervision, and used without any previous treatment, will be considered as items delivered by other participants and all procurement and transport fees will be paid to the Contractor.

12.14.3	Built in of concreted items

The Contractor must place all items that are built in to a place they are going to be built in, fastened i.e. strut them if required, and concrete them. Prior to concreting the Site Supervision will check and approve all elements to be concreted in.

The Contractor must keep all the items on places as per design and undamaged when concreting.

In all cases when built in items are used as anchors or holders, the Contractor is under obligation to inform the supplier so that he could perform the check after which the record will be made and signed by both sides.

Concreted items fastened by being pressed in the surface of fresh concrete (various anchors and similar) will be placed after vibrating the last layer, and before the concrete starts hardening. These items must be pressed so that the firm bond between the fresh concrete and concreted item is formed.

The unit rate for built in covers all work, material, equipment, transport, placing, fixing (including all position checks, axis, levels and other elements required for precise positioning of items), as well as all rectifications if any such are required.

12.15. CONCRETE CURING

12.15.1	General provisions

Curing refers to maintaining free concrete surfaces wet after cement binding at least 14 days after concreting.

The Site Supervision can shorten or prolong the curing period depending on weather conditions, type of used cement and concrete additives and air humidity in underground structures.

All concrete surfaces will be protected from direct sunlight at least three days after concreting.

12.15.2	Concrete curing by wetting

Concrete curing by wetting will be performed in one of the following manners: watering, spraying with water, making water pools, and covering with wet cloths and similar.

Water used for wetting must be in accordance with the requirements given in these Technical Terms.

In case the shuttering is wooden, it must also be kept wet throughout curing procedure. In case the shuttering is removed earlier, concrete surfaces are to be treated as free and kept wet until the end of curing procedure.

The concrete, especially the fresh one, must be protected from accidental damaging.

12.15.3	Membrane cover

In case the Contractor wishes to use the membrane cover, he will submit the proposal explaining the type of the cover, place, ways and terms of its use.

The use of membrane cover will be possible only if approved by the Site Supervision for each case separately.

12.16. LOW TEMPERATURE CONCRETING

Preparation, transport and built in of concrete at air temperatures lower than +5°C up to -10°C must be conducted in such a manner to provide concrete consistency, strength and impermeability.

The temperature during hardening procedure must provide concrete to achieve at least 50% of compressive strength before it is exposed to frost.

No frozen grains or ice cubes are allowed in aggregate during concrete preparation procedures.

At air temperatures lower than +5°C up to -10°C, the temperature of concrete mix must be at least from +6°C up to +9°C.

In order to achieve the required concrete temperature, its components must be heated up. When the air temperature is below -5°C, it is sufficient only to heat the water (not more than 80°C), and if temperatures are lower, small grain sized aggregates and possible 30mm fractions (not more than 70°C) must be heated up.

The measures must be taken that the concrete mix does not lose considerably in temperature during transport.

Concreting can be performed only if the surface concreted is above 0°C, i.e. if the temperature of surrounding ground mass is above 0°C. If that is not the case, the concreted surface must be heated to reach 0°C to a depth of at least 30cm. The heating temperature must not be over 90°C.

Concreting works performed at low temperatures will be accepted by a committee inspection.

The contractor is under obligation to rehabilitate the damaged areas as instructed by the Site Supervision.

12.17. CONCRETE SURFACE PROCESSING

12.17.1	General provisions

Surface processing will be performed in order to obtain smoothness to provide concrete creep along wetted surfaces, as well as prevention from damages and to obtain the required surface outlook.

Processing will be performed in accordance with these Technical Terms, depending on the position and purpose of concreted area during the structure exploitation.

All works anticipated by the Final Design as special treatment of concrete surfaces (painting, bitumen or epoxy resin covers, plastering, various insulations and other) are not referred to as surface processing here, but rather as additional works.

12.17.2	Concrete surface types

In accordance with position and purpose of concreted area during the structure exploitation, all surfaces are divided into:

- covered surfaces – the ones permanently filled

- visible surfaces – permanently free and visible surfaces on structures

- wetted surfaces – the ones in contact with water.

In all three types, the difference is made between the surfaces constructed with shuttering and the ones constructed without shuttering.

12.17.3	Free surface processing – no shuttering

Free surface processing will be performed along with the concreting, until the concrete is not yet bound at the surface.

Fresh concrete will be only leveled to required dimensions when it comes to filled surfaces.

If the visible surfaces are treated as exterior, the fresh concrete will be roughly smoothened. With free surfaces treated as interior, the fresh concrete will be smoothened so that smooth surface is obtained and thus grain removal from concrete prevented. If the surface is a base for various flooring or asphalt layers, it will be processed accordingly.

With free surfaces that are going to be wetted, fresh concrete will be manually or mechanically smoothened until no traces of smoothing are noticeable.

The cost of surface processing without shuttering is calculated in the cost of 1m of concrete and will not be additionally calculated for.

12.17.4	Surface processing – with shuttering

Surfaces which were under shuttering will be processed after shuttering is removed. Processing will be performed only on properly concreted surfaces and on the remaining ones after they are fixed.

Surfaces under shuttering that will be filled, no processing will be performed.

Visible surfaces under shuttering that are considered interior will also not be processed in case smaller voids are present on the surface and not distinctly visible from the distance of 3.0m.

In case this condition is not fulfilled, the Contractor must process these surfaces by filling the voids using materials containing epoxy resin (sica top and similar). Only the Site Supervision can make a decision if processing of these surfaces is necessary or not.

In case visible interior surfaces are a base for various wall covers (tiles, plastering, painting and similar), they will be processed accordingly.

The Contractor must process all surfaces that will be wetted in such a way to fill all voids and any other local roughness, and will smooth the surface using materials containing epoxy resin (sica top and similar).

12.18. ROUGHNESS

The Contractor is under obligation to construct flat, in shape and dimension, all concrete surfaces, apart from joints, as per drawings. Possible toughness must be within the limits given by these Technical Terms. In cases when roughness is greater than the required one it will be considered the concrete was not properly constructed and the Contractor will have to repair such surfaces.

Roughness will be checked by straight edge for flat surfaces, and by suitable equipment for round surfaces. Lengths measured will be 1.5 m for surfaces concreted without shuttering.

12.19. ALLOWED DISCREPANCIES FROM DESIGNED CONCRETE CONSTRUCTION DIMENSIONS

12.19.1	Dimension tolerances

For all concrete and reinforced concrete structures, the following discrepancy in dimensions of piers, beams, foundations, slabs and wall thicknesses are allowed:

- for covered surfaces	+12 mm – 6 mm

- for visible surfaces 	+6 mm – 3 mm

- for wetted surfaces 	+4 mm – 3 mm

(+) sign refers to element thickness increase and is names “positive tolerance”, and (-) sign refers to element thickness decrease and is named “negative tolerance”.

- The discrepancy from the designed			up to 3 m ± 3mm

direction at the base				up to 6 m ± 6 mm

- Discrepancy for all other deigned directions 		12 m and more ± 12 mm

taking into account that the maximum negative tolerance is conditioned by the element thickness that cannot be less than 97% of the designed thickness.

12.19.2	Roughness tolerances

Local roughness for surfaces under shuttering cannot exceed the following limits:

- for covered surfaces			±12 mm

- for visible surfaces 				±3 mm

- for surfaces in contact with water		±2 mm

In case dimensions and roughness are not within the tolerances, the Site Supervision will determine  whether it could be tolerated or considered as poorly constructed concrete (taking into account the other factors such as equipment, esthetics, stress in construction and similar)and whether he will require repair measures to take place in accordance with these Technical Terms.

12.20. TREATMENT OF THE CONCRETE NOT IN ACCORDANCE WITH SPECIFICATIONS

12.20.1	General

In all cases when the concrete quality is not in accordance with the requirements, the Contractor is under obligation to repair it as requested by the Site Supervision, or even to replace it. In case tests do show the quality to be good and visual inspection shows the work is not properly conducted, the Contractor is under obligation to repair the zones as required by the Site Supervision. Poorly constructed zones are considered to be the ones insufficiently compressed, containing segregated holes, as well as the ones with cracks, wet areas and bleeding which are the results of unprofessional work and/or disregard to provisions of these Technical Terms and the Site Supervision instructions.

Concrete repairs will consist of replacing the poor concrete or injecting it, and the Site Supervision can determine the combination of these two or introduce a third method not specified in these Technical Terms if they show to be inadequate repair procedures.

The new method can also be suggested by the Contractor but must be approved by the Site Supervision.

Any repair works are banned if not previously approved by the Site Supervision.

All costs of repairing and additional works will be fully covered by the Contractor.

12.20.2	Replacing poor quality concrete

The replacement of a poor quality concrete will be performed by chiseling of by any other appropriate method for poorly performed works. The Site Supervision will determine the maximum grain size and the filling procedure depending on the size of removed concrete. Procedures that can be applied are concreting or spraying.

The bond with the old concrete will be made by creating appropriate type of cuts. The Site Supervision can require the use of epoxy resin or similar material to be used on smaller cuts to enable better bond. Cut edges must be sharp with minimal depth along the edge line in depth of 1.5 of maximum grain size.

Prepared areas must be properly wetted before concreting starts and in case of epoxy resin, surfaces must be dry.

In case the poor concrete must be removed around areas of reinforcement or any other built in item, the Contractor must remove the concrete in such a way not to damage the reinforcement or any of the items and clean and prepare them properly for concreting.

In places where the surface of concrete to be replaced is considerably larger, the Site Supervision can ask for additional reinforcement, anchors and steel nets so to provide better bond between the old and new concrete. All work costs will be covered by the Contractor.

12.20.3	Injecting poor quality concrete

Injecting will be performed if control test results show the concrete is of a poor quality within the block, or in cases of wetting and bleeding.

Number, direction and dimensions of injecting holes, mix components and pressure of injection will be determined by the Site Supervision for each case separately with regard to position and dimensions of the zone in question and/or block and its purpose in the construction.  In cases of wetting and bleeding, injecting using special mixes and materials such as “syprogel” and similar will be applied.

The pressure of injecting will be such not to cause any further damage to the concrete.

All work costs will be covered by the Contractor.

12.21. MEASUREMENT AND PAYMENT

12.21.1	Measurement

Measurement for concrete works will be performed in accordance with the quantity of built in concrete within theoretical lines of shuttering and excavation, including the concrete built in at the approved cross-cuts.

Volume of built in reinforcement and other items and openings in concrete, whose individual volume is less than 2000 cm, i.e. individual surface less than 20 cm regardless to the length, will not be deducted from the quantity of built in concrete.

13. REINFORCEMENT

13.1	General provisions

Reinforcing works cover supply, cutting, forming, extending, bending, cleaning, placing and fastening of steel reinforcement.

Types and quality

All reinforcing works will be performed in accordance with drawings or as ordered or approved by the Site Supervision.

Naturally hard ribbed steel RA 400/500-2 and smooth steel GA 240/360 will be used for all reinforcing works.

Steel quality and its properties must be in accordance with all the requirements stated in the following rulebooks: BAB Rulebook, the Rulebook on Technical Regulations for the Use of Ribbed Concrete Steel for Reinforced Concrete and the Rule Book on Technical Measures and Terms for the Use of Net Reinforcement in Reinforced Concrete Constructions.

13.2	Supply and Storage

The Contractor must submit to the Site Supervision the Certificate of Compliance with every reinforcement supply. No supply or storage of reinforcement to site is allowed without the Certificate of Compliance. It is also not allowed to supply the reinforcement which is not in accordance with quality requirements.

Supplied reinforcement must be grouped as per bar radius and stored. It can be stored in open. All reinforcement must be placed on holders, which means storing on the ground is not allowed. If the Site Supervision does not order differently, reinforcement must be also stored per deliveries so that the same bar radius from a different delivery is not mixed. When it comes to deliveries from different manufacturers, i.e. of a different quality, the separation per quality is obligatory.

The Site Supervision can allow already prepared reinforcement to reach the construction site no matter if cutting and forming was performed by the Contractor or by a supplier.

If cutting and forming is performed by a supplier, the Contractor must enable the Site Supervision to perform the control of supplier’s workshop. That reinforcement must be stored separately as per items from detailed specifications. Certificates of Compliance for it must also be obtained.

Once the reinforcement is stored, the Contractor must place visible plates in the storing area, showing the radius of reinforcement, manufacturer and delivery date, as well as item number for each element.

The Contractor must deliver to the site sufficient quantities of all size reinforcement bars in order to be able to continue with works in accordance with the Programme even in cases when the Site Supervision, in accordance with the terms from point 0, stops the use of a certain delivery.

The Contractor must keep a diary on delivered, stored and built in reinforcement so that the Site Supervision can in any time determine the exact quantity of reinforcement on site.

13.3		Extending reinforcement

All reinforcement extension must be in accordance with detailed drawings, or as ordered and/or approved by the Site Supervision.

In case the Contractor wishes to extend the reinforcement in places not anticipated by detailed drawings, he has to get the approval from the Site Supervision before continuing with works. The reinforcement will be extended by overlapping and welding only if the Certificates of Compliance show the concrete steel can be welded.

13.4	Cutting, bending and placing of reinforcement

Cutting, bending and placing of reinforcement must be in accordance with detailed drawings, or as ordered and/or approved by the Site Supervision.

Bending will be performed cold. Cracked bars must be discarded and replaced with new ones.

Every bar must be cleaned from rust, oil, grease, dust and any other material that can cause poorer binding between the reinforcement and concrete.

Placed reinforcement must be properly fixed and tied. Fixing of reinforcement can be performed using steel and concrete pads, trusses and posts. The use of steel pads will not be allowed on external surfaces. Joining of reinforcement bars will be performed using binding wire and short welds.

For purposes of connecting the reinforcement in a unique grounding system, the Contractor will place appropriate welds on the reinforcement. The quality, thickness and distribution of welds will be determined by the Final Design.

Protective concrete layer will be 4 cm for wet area in contact with soil, unless shown differently in drawings. Allowed tolerance in protective layer thickness is ±0.5 cm. The discrepancy in distance from the designed one between two neighboring bars in a meter can be ±1/20, whereas the distance of every forth bar cannot be greater than the designed one.

The Site Supervision will inspect the reinforcement prior to concreting.

13.5	Preliminary and control testing

All manufacturers’ Certificates of Compliance for each new delivery are considered to be both preliminary and control testing.

The Contractor must perform preliminary and control testing of reinforcement extension by welding. Prior to works, as in all cases of technology change, preliminary testing on ultimate strength and breaking will be performed on ten samples for each bar radius.

In exceptional cases, when the Site Supervision questions the quality (difference in results given in Certificates of Compliance, considerably corroded bars and similar), the Contractor will have to perform control testing of such reinforcement.

Type of control testing in these cases will be determined by the Site Supervision. Tests that can be required are the following: testing of radius, ultimate strength and braking point, maximum stretching and bending properties. Control testing for ultimate strength, braking point and maximum stretching will be performed on ten samples and other testing on six samples.

All costs of preliminary and control testing of welded reinforcement joints will not be additionally paid for.

In case control testing for braking point and maximum stretching of welded joints give negative results, the Contractor will not be allowed further use of welded reinforcement.

In case the results of possible control testing required by the Site Supervision are negative, the Site Supervision will decide on further treatment of this reinforcement, including the possibility of issuing the order for its removal from the site.

13.6	Payment

Payment will be performed as per unit rate for kilogram of reinforcement.

The unit rate is for all works, material, equipment and other costs regarding supply, transport, storage, extension, cutting, bending, cleaning and placing of reinforcement, including welding for grounding and all trusses, posts and other reinforcement for the Contractor’s purposes and control testing.

14. WATERPROOFING WORKS

14.1	General provisions

Waterproofing works consist of material supply, equipment and all works including all necessary testing.

All works are to be performed as shown on drawings, described in physics of construction reports and in accordance with technical regulations:

- “Rulebook on Technical Measures and Terms for Roof Slopes” – Official Gazette SFRJ

- “Technical Terms for Performing Waterproofing Works on Flat Roofs” JUS.U.F2.02/1980

- “Rulebook on Technical Measures and Terms for Soundproofing of Buildings” Official Gazette SFRJ No. 14/82

- “Rulebook on Yugoslav Standards for Heat Technique in Building Construction” – Official Gazette SFRJ No. 69/87

Before insulation works start, already performed construction and other works must be check for irregularities because they might influence the quality, safety and lasting of waterproofing. In case any irregularity is noticed, it must be fixed before waterproofing works start.

Insulation works can only be performed on good quality surfaces as regulated by the Rulebook on Technical Measures and Terms for Bituminous Waterproofing of Roof and Terraces.

14.2	Bituminous waterproofing

14.2.1	Materials

Waterproofing materials must be delivered to site in their original sealed packaging. Domestic materials must be in accordance with the requirements of JUS U.M3.240, JUS U.M3.244, JUS U.M3.230, JUS U.M3.234, JUS U.M3.248 and JUS U.M3.232 standards.

For forming the slope on concrete surfaces where waterproofing is required, perlite concrete will be used.

14.2.2	Execution of works

Surfaces that are to be waterproofed must be clean, dry and smooth.

Holes, joints, voids, cuts and cracks must be filled and smoothened by cement mortar.

Waterproofing cannot be applied to wet surfaces.

Air temperature when waterproofing must be above +5°C. Same type of bituminous mix with appropriate bit-tape must be used in every work.

Bit-tapes will be placed by unrolling and pressing with the brush so there are no air bubbles left.

Bit-tapes must not get in contact whit each other. Overlapping areas are to be set in such a manner to provide the required number of layers.

Bit-tapes should be placed across the slope of the roof with the overlap in the direction of the slope itself.

Bit-tape is to be cut around ventilation and other pipes.

Minimum overlap when using bituminous tapes is 10 cm and maximum 15 cm.

All overlaps must be covered by bitumen in a layer of 1kg per 1m of the surface in equal layers. Both cover layers and bit-tape are to be pulled up to joints, up-stands and joints between the roof and the wall.

Up-stands (vertical roof parts) must have finishing layer made of glass wool and minimum 1.6 mm thick layer of special plastic bitumen.

The Site Supervision can require cutting of roof membrane in square size 30x30 cm up to construction before placing roofing tiles for the purposes of laboratory testing.

Laboratory test report will contain the following:

- Number of layers and material quality

- Bitumen weight in each layer and in total

- The size of overlaps

- Records in case there are voids

- Presence of foreign materials, bit-tape damages, etc.

The costs of testing will be covered by the Employer, unless the result is negative in which case the costs will be covered by the Contractor.

In the case of negative results, the Contractor will place additional layers until the work is approved. The cost of those works will be covered by the Contractor.

Guarantee period for those works must be at least 5 years.

After finishing the works, the Contractor will clean all surfaces and remove all material residuals as well as equipment.

14.3	Rigid waterproofing with penetrates

Rigid waterproofing by special mortars with penetrates, materials which under the influence of humidity penetrate several centimeters into the concrete, fill all voids and make concrete impermeable, will be performed on all reinforced concrete constructions where impermeability is required.

Waterproofing by penetrates is performed on the wet side of the wall. All pools, reservoirs and other parts of structures which hold water will be covered from the inside, and covered up walls protecting dry areas will be covered from the outside.

Generally, waterproofing mortars are applied on a wet, properly cleaned surface, free from any loose concrete parts. The Contractor must use the first class material and strictly follow the instructions when applying the chosen material.

15. METAL WORKS

15.1	General provisions

Details given in the Design are considered general. The Contractor must work up the details and submit them to the Site Supervision and the Designer for approval.

All works are to be professionally performed in accordance with the design, details and instruction of the Site Supervision using profiled steel, sheet metal and other materials.

Connections between certain elements are to be made by: welding (stapling), welding by cutting, closing up by rivets or screws and in accordance with the detail and the Site Supervision instructions. All welded parts must not have any roughness and joints must be hacked off. Rivets and screws used for joining steel parts of sheetmetal, white metal and galvanized parts, must themselves have galvanized heads. Pieces and parts must not be twisted.

All visible surfaces must be smooth and suitable for further work, painting etc.

Prefabricated elements must reach the site already once cleaned with the anticorrosive material.

Hardware, the principle of window and door opening and shutting   must be performed in accordance with specifications.

Prior to delivery, the Contractor must make a prototype of each type of doors and windows in order to be able to see all advantages and possible disadvantages. The Site Supervision will testify the functionality of the prototype and will give his approval.

Painting will follow the mantling.

Elements are first to be cleaned from rust, then protected, putty placed and after drying, and then honed. Thus prepared, elements are to be painted twice using the paint chosen by the Designer. Mantling of all galvanized and similar elements will be performed after all paint works are finished and the paint dry, just before taking over.

15.2	Payment

Payment will be as per unit rates for kilogram. Unit rates are for all works, materials, painting, recess cutting, built in, scaffolding and all other direct and indirect expenses.

16. TILING WORKS

16.1	General provisions

Material used for these works must be of a good quality. Tiles must be of a first class and paints as chosen by the Site Supervision. Prior to tilling, the following must be performed: checking of walls that are to be tiled (mortar is to be removed if any), checking the height up to which the wall is to be tiled, and removing all insufficiencies. Water and sewage conduits are to be tested.

16.2	Wall tiling with ceramic tiles

All wall surfaces are to be cleaned; the mortar from joints is to be scraped and concrete surfaces are to be roughened and washed by water.

Tiling is to be performed following the principle “joint onto joint” completely vertical and flat in all directions without waves. Damaged or deformed tiles cannot be used. Precise and regular openings are to be drilled in tiles.

After tiling, the walls are to be covered with white cement or gypsum, and joints are to be covered by aluminum or sheetmetal to achieve the black shade.

For complete work, material, equipment, transport, scaffolding and everything else, it will be paid per meter of tiled wall surface including deductions for all openings and voids.

16.3	Tiling of walls that are under water

This item refers to tiling of all vertical walls of filtering pools from the sand/coal level up to the top. Those walls are mainly under the water and therefore the procedure applied there will be somewhat different.

Whole tiles are to be pressed in a fresh cement mortar in the ratio of 1:2.

The base is to be applied to smaller areas so that it can be processed in one turn. Tiles are to be pressed with “open joints” which are later on covered by white cement.

16.4	Payment

Payment will be performed as per unit rates per square meter of tiled surface. Unit rates cover all work and material and all other direct and indirect expenses.

17. SHEETMETAL WORKS

17.1	General remarks

All works are to be performed using galvanized sheetmetal of 0.55mm or using aluminum unless specified otherwise. Joining is to be performed in such a manner to provide the stain for the sheetmetal.

All steel parts in connection with sheetmetal must be galvanized. Nails and rivets must of the same material as sheetmetal.

Is the base is of concrete, bricks or plaster, a layer of roof board (impermeable roof board) is to be placed under sheetmetal and its bottom side is to be covered by minium.

Rainfall gutters and covers are to be joined in a movable joint. At places where roof and walls meet, sheetmetal is to be lifted for about 20cm, and the edge is to be pulled under plaster.

When covering window shafts, joints are welded and sheetmetal is at the distance of 5 cm from the window and folded at least 4 cm. Sheetmetal must have overhang of 2.5 cm to 3 cm. If windows are made of aluminum, flashing is to be made of aluminum sheetmetal.

Drip is 3cm high with double layer from the inside and is tied to the nail which is in the wall by galvanized wire 1 mm in thickness which is welded to sheetmetal at the distance of 25 cm.

Valleys are to be flashed by sheetmetal. Sheetmetal will be fastened to the wall by nails and joints and also by standing seam at the distance of 8 cm under the edge of the cover. Sheetmetal is fastened using hooks made of the same material and chimney joints.

Eave face side flashed by galvanized sheetmetal will be 10 cm in height having standing seam when it comes to flat roofs. Sheetmetal is to be pulled under the cover for 10 cm, and upper edge is to be bent is circle. At the bottom of face side, the openings for water are to be made. Stiffening is to be achieved by pyramid trusts made of sheetmetal and welded to front and planceer piece.

Distance between trusts is 50cm. Everything as per detail.

Horizontal rainfall gutters are made of galvanized sheetmetal from 0.55mm to 0.60 mm in thickness with galvanized hooks of 30/3mm, with screws for roof construction on every roof tree. Distance between the hooks is 0.80 m to 1.0 m. Te connection to planceer piece must be made as well as tilt for water to be conducted to gutters 0.5 cm to 1 m.

Gutter joints are to be welded and riveted up, and if more than 15 m long, strains must be made.

Front edge is to be reinforced by steel bar Ø 6 mm. Horizontal gutters are made along with flashing of planceer piece made of galvanized sheetmetal 0.55mm to 6.0mm in thickness.

Gutter pipes are made of 0.55m sheetmetal and are fastened to wall by 25/5mm hooks on each 2m. Each pipe bending is to be considered as 0.5 m pipes. Pipe is to be placed 2cm from plaster.

Areas that are flashed more than 50 cm must be provided with trapezoid wood pieces at the distance of 50cm and made by standing seam in the width less than 50 cm by riveting and welding of joints and rivets.

All visible surfaces must be flat and at an equal distance from the wall.

Unit rate covers all preliminary and side works as well as surface preparing for flashing, recess cutting and similar which will not be additionally paid for. Neither will placing of roof board under the sheetmetal as required, minium cover and hole drilling be additionally paid for.

The same shuttering as for plastering are to be used. Sheetmetal tiles must contain the mark showing the thickness. Samples are approved by the Site Supervision.

All sheetmetal works must be cleaned.

17.2	Payment

Payment will be performed by unit rates per meter or piece as offered in the Bill of Quantities. Unit rates are for complete work and material and all other direct and indirect expenses.

18. CARPENTRY WORKS

18.1	General provisions

Carpentry is to be made using dry quality timber. Dressing is to be clean and smooth, and knots that do not stick out plaster.

White wood timber is to be soaked in the first class varnish. No added paints are allowed.

All joints must be glued. Strapping, door frames and all connections with walls must be concreted in full width and height. All oak fillets are to be fastened by brass screws.

Prior to painting, concreted surfaces are to be cleaned from mortar, soak in varnish and place putty. All surfaces are to be smoothened by glasspaper after drying off.

Surfaces prepared like this are to be painted by oily paint twice, covered with putty, smoothing after each layer and as final layer, applying matt varnish.

18.2	Hollow-core single door

On a frame made of fillets placed at the distance of 5 cm, two pieces of plywood of 8 mm in thickness is to be glued on either side. Three hinges of 110 mm are to be screwed in the door and fitted into the wing and door frame. Door handle of white metal is to be mantled along with cylinder lock with three keys. All metal parts are to be fastened by brass screws.

18.3	Payment

Payment will be performed per unit rate per piece. Unit rates are for all works and materials.

19. PAINTWORK

19.1	General provisions

Works stated here refer to all material supply and work execution as per drawings and the Site Supervision requirements.

19.2	Payment

Quantities for payment should be based on painted wall surfaces.

Paintwork includes material, instruments and works.

Payment will be performed per unit rates for square meter.

20. GLAZIER WORKS

20.1	General provisions

Glass used in the construction must be in accordance with JUS B.E.11 standard.

Minium putty is to be used for vitrification of steel doors and windows. Sash fillister must be cleaned before placing the glass and after the glass is placed it will be covered with varnish and then putty in thickness of 2 mm to 3 mm.

Sealing will be performed using molded rubber, minium putty or some other material as approved by the Site Supervision.

All necessary mantling and dismantling are calculated in the unit rate. After vitrification is finished window panes are to be cleaned.

20.2	Payment

Payment will be performed as per unit rates per square meter of vitrification surface. Unit rates are for all the work and material and all other direct and indirect costs.

21. ALUMINUM WORKS

21.1	General provisions

This item refers to the supply of material and instruments and work required for construction of aluminum equipment.

21.2	Classification

Works described here are divided into:

- Windows

- Solid door

- Glass door

- Vitrification surfaces

- Shades

- Concrete wall covers

21.3	Materials

Aluminum windows, doors and other constructions that are to be made of aluminum alloy of 16 KN/m of compressive strength and specific weight of 2.75 t/m. Surface must be enriched with eloxal layer in the color of aluminum.

Window and door construction should be reinforced by steel elements where necessary and stated in the design. Door and window frames and other concreted in elements in wall can also be made of steel but isolated by aluminum.

Glass can be fixed by rubber sealers if approved, or by special plastic materials.

Various fixing elements (screws, joints, nails, etc.) must be made of aluminum or some non-corroding material which will not damage the aluminum.

Glass has to be delivered along with aluminum construction and fixed by the same company.

21.4	Work

Aluminum works must be in accordance with schemes for aluminum works and approved samples, as per Site Supervision requirements.

The Contractor cannot perform any constructive changes without the approval from the Site Supervision.

During the works, the Site Supervision can perform the check of materials,  constructions and work itself in Contractor’s workshop and remove all parts and items that are not suitable which will be replaced by the Contractor.

The Contractor must pay attention to storekeeping of aluminum equipment and to draw the Site Supervision’s attention to any irregularities. The equipment is finally taken over when completely finished, i.e. built in.

21.5	Payment

Payment will be performed as per constructed quantities using unit rates.

- Windows

- Solid doors

- Glass door

- Vitrification surfaces

- Shades

- Concrete wall covers

Unit rates cover whole material, instruments, work, hardware, vitrification and final processing of the item and built in as per schemes for aluminum works and as requested by the Site Supervision.

The costs of heat insulation will be included in this item as approved.

22. OTHER WORKS

22.1	General

After all works are finished, the Contractor must clean the whole structure, clear the site and transport the residual materials to a waste dump outside the settlement.

The Contractor must also perform small unpredictable works. All those works must be as instructed and ordered by the Site Supervision.

23. REINFORCED CONCRETE CONSTRUCTION REHABILITATION

23.1	General provisions

The Rulebook for rehabilitation, reinforcement and reconstruction of structures in seismic areas of VII, VII and IX zones per MCS scale is to be followed. The same rulebook is to be followed for structure rehabilitation which are not built as non-seismic constructions and are in the aforementioned area. The provisions of this rulebook are applied to reconstruction of old civil construction structures.

23.2	Materials, construction, protection, control

Mortar for rehabilitation of concrete surfaces should contain cement and polymers. It should be made mechanically in smaller quantities, sufficiently to be built in before it started binding.

Prior to any coat, the surface must be prepared. It is important that the surface is cleaned from corrosion, old paint layers, grease and similar. At places where concrete damages are noticed, such as protective layer falling off, segregation or poorly performed joints, it is necessary to remove the damaged concrete. The works are to be performed using manual instruments, and then to recess cutting or some other suitable procedure. The attention is to be made not to damage the reinforcement, and chase sides are to be cut to reach sound concrete. All reinforcement and chases are to be cleaned from loose concrete, impurities and grease. They need to be prepared for applying the repair mortar. The use of manual instruments (brushes, broad knife and similar) including manual washing is anticipated. Sandblasting will be performed on larger surfaces where possible. The estimate is that the sandblasting can be used to clean 70% of total surface anticipated for cleaning. Sandblasting is to be performed in accordance with SiS standard 05-59-00/67 with cleanness degree: SA-3, SA-2.5 and SA-2.

Surface where mortar is to be applied must be properly wetted at least one hour before application. The use of primary coat at contact of old with new, where thick layers of mortar are to be applied, is recommended.

Primary coat is to be made of cement, sand, water and polymer.

Mortar thickness applied in a single layer should not be more than 3cm. Greater thickness is to be applied on two to three layers.

Mortar curing after application should be conducted by covers that are to be maintained wet or by spraying for minimum of 24 hours.

All rehabilitated concrete surfaces should be protected by cement and polymer coat. Coat is to be applied in three layers and cured for at least 24 hours.

This coat is to be used on new reinforced concrete elements.

For rehabilitation by injecting, all injection mixes determined by the design based on the type of damage will be used.

Injection mixes are:

- solutions of certain viscosity, for cracks and opening smaller than 0.4 mm

- suspensions, for injecting cracks and openings from 0.4 mm to 5 mm

- liquid mortars, for cracks and openings larger than 5 mm

Following cement types are used as binders for suspensors and technical mortars

- portland -  cement and portland – cements with mineral additives in accordance with JUS B.C1.001 standard

- portland -  cement and portland – cements with mineral additives in accordance with JUS B.C1.011 standard, with improved mix for which additional terms of grinding are applied – residuals on sieve size 0.09 mm cannot be more than 5% and specific surface must be larger than 4000 cm2/g;

- sulfate-resistant cement, in accordance with JUS B.C1.014 standard

- aluminum cement, in accordance with JUS B.C1.015 standard

- colloid-cement – finely ground portland – cement , portland – cement  with mineral additives in accordance with JUS B.C1.014 standard with additional conditions - residuals on sieve size 0.045 mm cannot be more than 5%; this cement must be water absorbent

- expanding cement fulfilling the requirements for portland – cement with mineral additives in accordance with JUS B.C1.011 standard, showing controlled expansion in moist surrounding.

Part 2 – CCMS

- HYDRAULIC AND CIVIL ENGINEERING PART

- DESCRIPTION - HYDRAULIC AND CIVIL ENGINEERING PART

- Introduction and background

The existing public water supply system for Krusevac is based on raw water abstraction from the impoundment Celije. In 1984 the system was put in operation including the dam, raw water pipeline, WTP Majdevo, treated water transmission mains and distribution network.

The aforesaid communal water supply system for Krusevac is closely inter-connected with the Regional Water Supply System for Rasina and Morava Districts (in further text Regional System). The Regional System includes all bulk-water supply elements, such as:

- Impoundment

- Dam

- Water intakes

- Raw water pipelines

- Water treatment facilities

- Treated water transmission mains

- Control and regulation elements

Physical boundaries of the Regional System are defined at the connection points to particular local communal systems for individual municipalities. These connection points must be controlled and regulated in order to ensure stability of the Regional System and its optimal operation and management.

The Regional System is highlighted in the Water Management Master Plan of the Republic of Serbia as one of strategically important integral regional water management systems that serve a multitude of municipalities and a large number of local population and district industries. The Regional System is planned to supply a number municipalities in the region, including: Aleksandrovac, Krusevac, Trstenik, Varvarin, Cicevac, Paracin, Cuprija, and in a long run Razanj and possibly Jagodina.

At the moment the municipalities of Aleksandrovac, Krusevac and partially Trstenik are supplied from the Regional System, while some of the aforesaid neighbouring municipalities face serious water supply shortages.

Based on the request by district municipalities, in 2007 a Feasibility Study was conducted by the EU-funded MIASP programme in order to investigate feasibility of the Regional System upgrade and extension towards municipalities of Cicevac, Varvarin, Paracin and Cuprija. The proposed Project proved to be technically and financially feasible, and the Feasibility Study was consequently approved by the Delegation of European Commission and recommended for further implementation by the Steering Committee including the Ministries of the Government of Serbia and representatives of the EC.

This particular part of the project includes works and equipment that are necessary for appropriate remote control and operation of the Regional System. More specifically, this section of the project encompasses elements in the Regional System that enable adequate control and operation hydraulic parameters towards particular municipalities. These elements include the following:

- Measurement and control block Krusevac

- Measurement and control block Cicevac

- Measurement and control block Stalac

- Measurement and control block Varvarin

Measurement and control block Krusevac provides the overall control of flows and pressures at the main transmission pipeline towards downstream municipalities, while measurement and control blocks Cicevac, Varvarin and Stalac control flows towards individual supply zones. Each supply zone (Cicevac, Varvarin, and Stalac) is to be connected via appropriate terminal connecting tank.

2	Technical description of the sub-system Krusevac-Varvarin-Cicevac

2.1	Technical concept

2.1.1	Planned and as-built status, boundary conditions

This section presents basic technical features of planned and constructed elements which are of significance for proper operation of the sub-system Krusevac – Varvarin – Cicevac.

2.1.2	Water Storage Tanks

The following table presents basic technical features of water storage tanks that are relevant for proper operation of the sub-system Krusevac – Varvarin – Cicevac. These tanks represent essential boundary conditions for the sub-system operation, uniform flow regimes and transient flows in the transmission mains.

It is important to stress that all major water supply zones are to be connected to the Regional System only via appropriate terminal water storage tank that also serves as a local water distribution tank. This is an important pre-requisite for stabile, safe and reliable operation of the Regional System.

Planned and as-built status of water storage tanks

| No | Name | V (m3) | Zmin(masl) | Zmax(masl) | Status | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Lipovac | 5.000 (+5.000 phase II ) | 210,00 | 215,00 | Planned |  |
| 2 | Todorova kula | 400 | 202,00 | 206,00 | Constructed | Inlet piping to be adjusted |
| 3 | Ćićevac | 400 | 202,00 | 206,00 | Constructed | Inlet piping to be adjusted |
| 4 | Varvarin | 4.000 | 192,00 | 196,00 | Planned |  |

2.1.3	Transmission mains

This section presents major technical features of the transmission mains that are of relevance for proper operation of the sub-system Krusevac – Varvarin – Cicevac, and hence for normal control and operation of the Regional System.

Transmission mains – planned and as-built status

| No | Section | DN(mm) | L(m) | Pipe material | PN (bar) | Status |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | WT Lipovac – connection to existing transmission main DN1.000 | 1.000 | 505 | DI | 10 | Planned |
| 2 | Lipovac-Dedina | 1.000 | 6.531 | Steel, concrete | 10 | Constructed more than 90% |
| 3 | Dedina-Stalać | 600 | 11.081 | GRP | 10 | Constructed more than 90% |
| 4 | Stalać-Varvarin | 400/352,6 | 5.359 | HDPE | 10 | Planned, partially constructed |
| 5 | Stalać-branch to WT T.kula | 400/352,6 | 710 | HDPE | 10 | Constructed |
| 6 | Stalać-Ćićevac | 400/352,6 | 6.515 | HDPE | 10 | Planned, partially constructed |
| 7 | Branch to WT Todorova kula | 200/163.6 | 644 | HDPE | 10 | Constructed |

2.1.4	Basic hydraulic features of the sub-system Krusevac-Varvarin-Cicevac

- This section presents an overview of basic hydraulic features of the sub-system Krusevac – Cicevac – Varvarin that are of importance for proper control and operation of the Regional System.

- The sub-system Krusevac-Varvarin-Cicevac is planned to be developed in two stages:

- Stage 1 – transport of water by gravity only – within the scope of this project

- Stage 2 – introduction of a booster pumping station – out of the scope of this project

Only stage 1 is in the scope of this project, and therefore stage 2 has not been considered.

The total capacity of the sub-system Krusevac-Varvarin-Cicevac in the stage 1 – gravity transport is 125 l/s for Varvarin and Cicevac, plus 8 l/s for local villages Bosnjane and Maskare.

Stage 2 of the sub-system Krusevac-Cicevac-Varvarin (out of the scope of this project) allows for the capacity increase up to app. 260 l/s by introduction of a booster pumping station.

2.2	Control and operation concept of the Regional System – sub-system

The basis for the control and operation concept is adopted based on the proposed hydraulic concept of the sub-system.

Proposed hydraulic concepts enables for almost uniform flow regime in the Regional System. All major supply zones are to be connected to the Regional System via corresponding terminal connecting tanks. In such a way, the Regional System is hydraulically separated from local distribution system, which enables adequate control and operation of the Regional Scheme.

In water storage tank Lipovac continuous water level monitoring is envisaged, including its full operational scope (0-5m, i.e. 210,0 to 215,0 masl). In the zone of higher water levels, at the level of 4.90m the alarm should be activated in order to prevent unnecessary overflows and water losses. Another alarm is supposed to activate at low levels (H=1,0m, i.e. Z=211,0 masl), in order to indicate very low levels in the tank. At the outlet pipe of the tank there is a provision for measurement of residual chlorine concentration in order to be able to adjust it, as required.

At the downstream part of Krusevac water distribution system, opposite Makresane settlement, it is planned to install a measurement and control block Krusevac. Primary role of this measurement and control block (MCB) is protection of the water distribution system Krusevac from downstream disturbances, and the overall control of flows towards the downstream municipalities. This MCB includes two branches with electro-magnetic flow meters and corresponding regulating needle valves. The operational regime of this MCB should be flow-control based, and also accorded with MCB-s Varvarin, Cicevac and Stalac.

At the pipelines supplying Varvarin (HDPE DN400), Ćićevac (HDPE DN400) and Stalać (HDPE DN200), it is planned to install separate MCB-s. Each of the aforesaid MCB-s consists of two branches (one duty, one stand-by) with regulating needle valve and flowmeter at each branch. Basic regulating parameter is flow which is maintained nearly constant. It is also envisaged to monitor operational pressures upstream and downstream of the regulating valves.

After the MCB-s, inlet pipes are supplying connecting tanks; Varvarin, Ćićevac and Stalać. Each of the aforesaid tanks includes continuous water level measurement, as well as monitoring of residual chlorine concentration.

Structures for installation of measuring and control equipment in the sub-system Kruševac – Ćićevac – Varvarin

The aforesaid MCB-s are located at the upstream ends of the pipelines supplying Varvarin, Cicevac and Stalac.

The MCB structure represents a reinforced-concrete structure which accommodates mechanical, process and instrumentation and other electrical equipment. The following table presents basic structural characteristics of these structures:

Basic structural features of MCB structures

| Name | Internal dimensions | Z pipe centreline (masl) | Z bottom slab (masl) | Z top slab (masl) | d bottom slab (cm) | d upper slab (cm) | d walls (cm) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Varvarin | 6,0x2,5m | 133,76 | 132,96 | 135,66 | 30 | 20 | 25 |
| Ćićevac | 6,0x2,5m | 132,55 | 131,75 | 134,45 | 30 | 20 | 25 |
| Stalać | 5,0x2,5m | 132,55 | 131,75 | 134,45 | 30 | 20 | 25 |

These structures are cast in-situ reinforced-concrete vaults with defined pipe penetrations and openings for access and equipment installation and maintenance. The openings for equipment installations are equipped with frames and chequer-plate covers. The access openings are equipped with frames and steel chequer plate covers for light traffic loading with internal dia. 600mm clear opening.

Base slab includes a sump for a drainage pump, sized 50x50cm and 40cm deep. Diagonally, ventilation pipes DN100 are to be installed, as indicated in the drawings.

The vault is founded on a compacted natural gravel layer 10 cm thick and a layer of mass concrete grade 15,5 cm thick.

II.	CIVIL ENGINEERING WORKS

## 3.1	Application of the Specifications and Appendices

This Technical Specification Civil Engineering forms an integral part of the Contract/Tender Documents.

The provisions of these specifications shall be read and construed with the Drawings, the Bill of Quantities and other technical specifications forming part of the Tender/Contract Documents.

Specifications for earthworks, concrete works, masonry and all other Civil that are relevant to execution of road works, external piping, electrical and mechanical works are hereby deemed fully applicable to such other works.

Standards and Codes of Practice are listed in Appendices to this Chapter 3 and are considered an integral part of these TS.

## 3.2	Earthworks

### 3.2.1	General

#### 3.2.1.1	Scope

These specifications refer to common earthworks for building constructions. Special preparation works such as building, demolition or special supports required due to proximity of buildings or work under the level of the aquifer shall be specified in the special specifications.

#### 3.2.1.2	Definitions

  - Earth and soil - the terms refer to any type of natural material, including rock.

  - Layer thickness - is the thickness after the compression and compaction, to be carried out according to the specifications pertaining to that layer.

  - Back-fill (borrowed fill) - soil taken from the building site for filling purposes.

  - Brought up fill - fill brought from places out of the building site for filling purposes.

  - Surplus soil - excavated soil not used in the construction.

#### 3.2.1.3	Standards

The following is the main standard pertaining to this paragraph.

Sorting of soils according to:

  - JUS Code U.B1.00

  - Euro Code ICS 91.100.15

  - AASHTO ASTM-D-3282

#### 3.2.1.4	Other Paragraphs

All the provisions in the paragraphs of the general construction works specifications, as detailed below, are also applicable to the present paragraph.

  - Section 3.4 - Cast In-Situ Concrete Works

In case of contradiction between the above standards the local Serbian standards shall predominate.

#### 3.2.1.5	Casing and Support

The sides of excavations shall be cased and supported, in case that the soil requires casing, whether the Engineer has required that this be done or not. The boards and supports shall be sufficiently strong and rigid to sustain the pressure of the soil and prevent collapse or horizontal movement of the casing. Alternatively, if soil conditions permit it, the Contractor shall be able to shape the sides of the excavations according to their natural slopes, instead of casing and supporting the soil.

#### 3.2.1.6	Responsibility for Stability

The provisions included in these specifications are guidelines for the best professional execution. Carrying out these instructions is not enough to  absolve the Contractor of his legal responsibility, and he shall be solely responsible for the stability of the excavation and the safety of the earth works carried out at the site, including safety of the structures and the roads in the vicinity of the site, and all that this entails.

#### 3.2.1.7	Collapse

In the event of a collapse due to insufficient support, or any other reason, the Contractor shall re-excavate the pit and repair the casing and support. Moreover, the Contractor shall bear the cost of all damages to people or property incurred by the collapse which may arise in this context.

#### 3.2.1.8	Drainage

All excavations described above shall be protected against the penetration of rainwater, by the adoption of appropriate means such as excavation of drainage trenches, or the creation of temporary earth banks. If rainwater or sewage water has accumulated in the excavated pits, despite the means adopted by the Contractor, the Contractor shall remove the water from the excavations and allow the bottom to dry sufficiently, to the Engineer's satisfaction, before he resumes work. These instructions also apply to excavation in back-fill areas etc.

The excavation and fill and excavation in back-fill areas etc. shall be carried out in such a way as to allow constant drainage of the water during all the stages of work. The means of drainage shall include works as excavation of temporary trenches, building of banks, pumping of water, blocking of pits, etc.

#### 3.2.1.9	Ground Water

When work is carried out in areas where ground water is expected or where ground water was detected during work, the Contractor shall pump the water by the means and methods approved by the Engineer. The pumping shall be consecutive and sufficient for ensuring dry area, as required for carrying out the work. The Contractor shall also take care to dispose of the pumped water to a site selected at his own responsibility, with the approval of the Engineer given in advance.

#### 3.2.1.10	Coordination and Disturbances

The Contractor shall carry out the work in coordination with the operating conditions prevailing at the site, including the function of electricity, water, irrigation and sewage systems, etc., subject to the directions of the responsible authority. Moreover, coordination and cooperation must be ensured with other parties or Contractors working at the site. The Contractor shall take all means required to prevent disturbances and holdups of traffic, including marking with lamps and flags, signposts and the positioning of permanent employees to direct the traffic, etc.

Special requirements and limitations shall be defined in the special specifications.

In built areas and populated areas, the Contractor must carry out the work in such a way that all in situ systems shall continue to work and function without disturbance, including access to buildings, free pathways and the proper function of electricity, water, sewage and irrigation systems.

#### 3.2.1.11	Returning the Area to its Former State

The Contractor shall return to its former state, any area dismantled or damaged following preparation, dismantlement, or cleaning works, or earthworks of any kind, for any purpose whatsoever, including in-situ installations such as cells, trenches, drainage installations, etc.

In addition to the above, in paved areas, the Contractor shall apply all of the paving layers - asphalt, concrete tiling of various types, etc.

The area shall be returned to its former state by means of new materials and   products, except where the Engineer has approved the use of materials and products from the dismantlement.

### 3.2.2	Preparation and Dismantling of Works

#### 3.2.2.1	General Earthworks

Before starting the Earthworks (excavation and fill) the Contractor shall carry out all the works required below (removal or exposure of vegetation, removal of waste and obstacles), as well as additional works, as required by the drawings, so that the soil surface obtained shall be free of shrubs, weeds, structures, pipes, concrete wastes, etc.

The execution schedules of each of these activities shall be determined by the Contractor; in no case shall an area in which the vegetation has been removed be exposed.

#### 3.2.2.2	Removal of Vegetation and Cleaning

Removal of vegetation and cleaning, involves the uprooting of existing vegetation (shrubs and weeds) including its roots, and removing and dispersing it. The cleaning of the area includes removal of any garbage or alluvial sedimentation and their disposal as detailed in sub-clause 3.2.2.7 below.

#### 3.2.2.3	Exposure

Exposure includes removal of existing vegetation (shrubs and weeds) and the upper soil layer, up to a thickness of 20 cm, and then disposal and distribution of this layer as described in sub-clause 3.2.2.7. Exposure shall be carried out according to a plan, or after the Engineer has approved the execution and its scope in advance.

#### 3.2.2.4	The Cutting Down and Uprooting of Trees

- Cutting-Down Trees

Any vegetation, whose bark circumference is at least of 20 cm at a height of

1.0 meter above ground, shall be considered a tree. Any tree whose circumference is less than 20 cm shall be considered vegetation (sub-clause 3.2.2.2 above). If a number of tree trunks branch out from the same root, i.e., originate from the soil, each one of them shall be considered as a separate bark, if it complies with the above definition.

The Contractor must cut the trees close to ground, but not less than 5 cm. from the surface. If it has not been specified otherwise, the Contractor shall cut the trunks and branches with a circumference of 200 cm and above, into segments of 1.0 to 2.0 meters. Trunks and branches, with a circumference less than 15 cm, shall be removed as detailed in sub-clause

- Uprooting Tree Stumps

In the event that the Contractor received an area with the stumps of trees cut down by others to a height of 5 cm at least, and not arched before they were cut, and the circumference of their section at the cutting level is greater than 15 cm., shall be considered, for the purpose of uprooting, as if they were trees with a circumference of 20 cm diameter at a height of 1.0 meter.

Tree trunks that have been cut shall be uprooted and removed as described in sub-clause 3.2.2.7. The pits created by the uprooting shall be filled with the best local back-fill or with brought up fill, which shall be compacted in 20cm thick layers, up to the planned level of the excavation (or the natural ground level, if there is no excavation). If required, the pits shall be sprayed with a weed killer (see sub-clause 3.2.2.5 below).

- Trees Uprooting

If not stated otherwise, the work of uprooting trees shall include all the works included in the above sub-clauses of uprooting and cutting, but the works may be carried out in the order suitable to the Contractor. In the event than the entire job consists of uprooting alone, it shall be classified as a separate job.

#### 3.2.2.5	Weed Killers

Areas covered with weeds, areas from which the vegetation has been removed, exposed area and the pits from which trees have been uprooted shall be sprayed with a weed or root killer. The spraying shall be defined in the contract document. The Contractor must locate and define the weeds at the site and find the appropriate chemical material for killing that specific type of vegetation. The herbicide shall be sprayed by a Contractor authorized to carry out such work by the Ministry of Agriculture.

The Contractor shall make sure that the wind conditions are appropriate for spraying and shall ensure that no environmental damage is caused.

#### 3.2.2.6	Dismantling

  - Dismantling of Existing Structures

Wherever required to do so, at whatever length and depth, the Contractor shall dismantle both surface and underground structures, such as; existing concrete trenches, sewage pits,  drainage lines containing concrete pipes and stone fill, aqueducts, control-cells, embankments and the like. The work includes removal of concrete and stone pieces, etc. as detailed in sub-clause 3.2.2.7 below.

- Dismantling Pavements

If required, concrete pavements and asphalt pavements shall be dismantled along their entire constructional depth down to the subgrade. In asphalt pavements, if dismantling is needed for laying a new road or for repair - the asphalt layer shall be sawn off within the dismantling boundaries. Dismantling the pavements shall include disposal of the waste from the area according to sub-clause 3.2.2.7 and compaction of the surface after dismantling, until the required density is obtained. When dismantling concrete plates, the plates shall be broken into parts small enough to be loaded and disposed of.

- Blocking of Pits and Trenches.

The Contractor shall use local back-fill of the quality approved by the Engineer. In order to block any pits or trenches created following the above dismantling. The Contractor shall compact the fill in layers up to the required level, according to the plan.

#### 3.2.2.7	Disposal of Waste

The waste shall be disposed according to the provisions of Chapter 1, Description of Project.  The disposal of waste shall be the sole responsibility of the Contractor.

### 3.2.3	Excavation Works

#### 3.2.3.1	General

If the ground preparation works (such as the removal of vegetation, the uprooting of trees, etc) have caused such changes in the topographic state as to require renewed Surveying- the Contractor shall be obliged to survey and mark again.

#### 3.2.3.2	Types of Soil and Earth

The present specifications classify the soil and earth into two types only: rock or any other soil. A rock shall be considered any continuous layer of solid rock or large stone slabs, which can only be quarried by means of penetrate-meters, compressors, wedges, sledgehammers, etc.

Any soil, which may be handled with tractors of all kinds, even when operated in their strongest gear position, shall not be considered rock. The term "excavation”, in all of the sections of these specifications, shall relate to quarrying in rock, even if this has not been explicitly noted in each section.

Thus, all of the sections referring to excavation works in these specifications also apply to quarrying, subject to the additional requirements presented in clause 3.2.4 below.

#### 3.2.3.3	Excavation

- Area Excavations

Excavation in the area shall be carried out according to the details of the drawings, or as required in order to lower the level of the existing soil surface, down to the levels determined by the contract drawings. In the case of soil surpluses, the best excavated soil which may serve as an appropriate fill, shall be transferred to the planned fill areas and distributed there as provided in the section concerning fill.

- Excavation Below the Required Level

In the event that the excavation has been performed by the Contractor to a depth greater than required, the Contractor shall refill it up to the required levels with an appropriate fill material as specified. This fill material shall be free of stones, silt, organic material, etc. and shall be distributed in layers no thicker than 20 cm.

Mechanical compacting tools shall be used to compact the layers after sprinkling an optimum amount of water.

The compaction shall proceed until the natural density characteristic of soil at this depth is achieved. Any voids created following excess excavations below foundations, etc. shall be filled with lean concrete. The provisions of this section also apply to excessive excavation, even in a multi- layer rock.

- Digging of Trenches

If not stated otherwise, an excavation no wider than 2.0 meters, whose depth is no less than 50 cm. below the original soil surface shall be defined as a trench. The bottom and sides of the trench shall be shaped to the desired gradient.

- Excavation of Basements

Excavations for basements and subterranean structures shall be carried out according to the dimensions specified in the drawings and with consideration for the ground conditions, the work spaces and the need for casing, formworks, supports, sealing and any other goal (see sub-clause 3.2.1.5 above and sub-clause 3.2.3.3 below). The earth from the excavation shall be temporarily stored in nearby heaps. The bottom of the excavation shall be shaped according to the required levels and gradients and shall be compacted as detailed in sub-clause 3.2.1.5

The best the excavated soil shall be used both for back-fill as detailed below and for fill in any other place in the site.

The back-fill around the external walls shall only be carried out when all of the works to be covered with soil are completed, and after all of these works have been inspected and approved by the Engineer. The back-fill shall be comprised of layers, whose thickness after compaction shall not exceed 20 cm, as detailed in sub-clause3.2.1.5. The back-fill restored along structural walls coated on the outside with sealing layers, shall be free of stones and large clods or any other waste liable to damage the sealing and the entire work shall be carried out with proper care.

- Workspaces

Workspaces for the purpose of casing, formworks, sealing or any other purpose, in all types of excavation and quarrying works, shall be determined by the Contractor according to need, as stated above.

#### 3.2.3.4	Transferring the excavated soil

The Engineer or Geotechnical Engineer shall determine the type of soil, the part of the soil to be transferred to other places, the part to be used for fill and the part to be disposed. When the soil surplus intended for transfer is placed in a heap, care should be taken to ensure appropriate drainage arrangements.

The Contractor shall remove any soil surplus outside the site, as described in detail in the STS.

### 3.2.4	Filling with Soil

#### 3.2.4.1	General

The best soil approved as fill shall be brought from the excavation areas and spread in the layers and levels specified in the plan, then compacted to the required density and moisture.

#### 3.2.4.2	Borrowed Fill

Should the best of the excavated soil prove insufficient for filling, the shortage shall be made up with soil borrowed. The selection of a place in which to excavate borrowed fill and the quality of the soil taken from that place, both require the Engineer’s approval. Filling with borrowed fill shall be carried out as detailed in regard to filling works above.

#### 3.2.4.3	Brought up Fill

In the absence of appropriate local soil suitable for making up the shortage of soil for filling, clean soil, free of stones, silt, organic materials or any other undesirable material, shall be brought from outside the site.

The imported soil and its source shall conform to the requirements of the specifications and require the Engineer’s approval.

#### 3.2.4.4	Approval of Excavation and Filling

The bottom of the excavation and the fill surface and the various types of bedding, as detailed below, require all the Engineer approval.  Casting, or the works of covering the castings, shall not be commenced without the Engineer approval. When required, trenches and pits shall be wetted before the casting.

### 3.2.5	Compaction and Tamping

#### 3.2.5.1	General

A distinction shall be made between controlled compaction and regular compaction. Regular compaction shall be carried out on layers of quarried material, which cannot be tested under controlled compaction. The excavation sub-grade (the final level after the earthworks have been completed), the fills and any other area marked in the drawings or in any of the other contractual documents, shall be compacted with appropriate mechanical equipment, at the level of wetting required in order to attain the required level of density. The moisture content shall be in the range of 2% from the optimum moisture content.

1st. The compaction shall be carried out by means of various types of mechanical rollers, after the soil has acquired the required moisture content (through the addition of water or by drying). The rollers shall be pneumatic, vibrational, lamb's feet, etc.

In those places where the various types of mechanical equipment cannot be applied, the compaction shall be carried out with special equipment such as frog clamps and the like.

Unless otherwise specified, the compaction shall be carried out in layers no thicker than 20 cm. (after compaction).

Before compaction of each layer, it must be leveled. The finish of the upper layer compaction shall be within the allowed deviation limits.

The compaction work includes preservation of the finished layer surface and its edges, at the appropriate density and humidity and at the proper height until it is spread and compacted onto the next and proximate layer. The preservation of the layer surface also means repeated wetting and compaction if required to this end.

#### 3.2.5.2	Tamping of Areas

Tamping of the subgrade surface inside the excavation or tamping of the existing soil surface or the soil after stripping - shall be carried out by ploughing and raking, wetting and tamping the soil, until a 20 cm. thick layer is obtained, compacted to the required level of density.

Unless otherwise specified, in those places where the thickness of the fill is less than 20 cm. (after compaction) the Contractor shall plough the natural soil surface to such a depth that after the distribution of the fill layer, its mingling with the plowed soil surface and its compaction, the obtained layer shall be 20 cm. thick.

#### 3.2.5.3	Compaction Overlap

In all types of compaction, the compaction overlap in a mechanical or vibrational roller, at least half the width of the back wheel, and in a pneumatic roller, half the width of the back axle.

#### 3.2.5.4	Collection and Testing of Samples

Compaction control process shall be prepared and carried out by the Contractor, while the location and the number of sampling points shall be approved by the Engineer. Compaction control shall be carried out in series, with minimum 5 tests per series.

One of five test results per series, according to the absolute value, may vary by maximum:

- 5% when measuring volume weight in dry state

- 10% when measuring the compaction module Ms

The Contractor shall submit the test results for each layer to the Engineer in writing, and the Engineer shall be entitled to request additional testing for control tests in case of doubt in compaction quality.

The wetness of the fill material shall be approx 2% above or below the standard Proctor test, and it shall be even throughout the entire layer. The required minimum volume weight of the filled material in dry state shall be 95% of laboratory compaction according to the standard Proctor test.

The following standards shall be used for compaction control:

- For sampling: JUS UB1 010

- For ground wetness: JUS UB1 012

- For ground bulk weight: JUS UB1 016

- For compaction module: JUS UB1 046

Compaction equipment for the earth-fill construction material shall not be used unless approved by the Engineer in writing.

Depending on the areas to be compacted and the prevailing conditions, compaction equipment shall comprise vibrating or non-vibrating steel or pneumatic tire rollers, hand-operated rollers, mechanical tampers and other compaction equipment or methods approved by the Engineer.

### 3.2.6	Wrapping and Bedding

#### 3.2.6.1	Wrapping

Wrapping around pipes, control cells, foundations, walls etc., submerged in clay soils, shall be made of sand, gravel-sand, or other granular soil authorized to this end, all according to the specific case, as required in the drawings or in one of the other contractual documents.

The wrapping material shall be clean of clay, silt and damaging materials and free of stones. Detailed instructions regarding the method of execution shall be given in the special specifications.

#### 3.2.6.2	Sand or Fine Gravel Bedding

Sand or fine gravel bedding below concrete surfaces, floor tiles or foundations shall be applied at the thickness marked in the drawings. The above materials shall be taken from an authorized source and shall be course as, free of all stones, clay, silt, organic materials or any other damaging materials.

The above materials must be spread in layers whose thickness does not exceed 20 cm, and compacted as detailed in clause 3.2.5. The layers shall be spread in parallel with the final surface of the cast or tiled area, and the bedding surface shall be shaped according to the required levels and gradients. Bedding made of another material shall be carried out according to the special specifications.

## 3.3	Cast on Site, Concrete Works

### 3.3.1	General

#### 3.3.1.1	Scope

This paragraph deals with the quality of the materials and workmanship of concrete and reinforced concrete works, performed in accordance with the drawings and according to the Special Specifications, and shall apply to all parts of the building, underground and above, for the whole site at any given depth or height. The specifications apply for ready mixed concrete and concrete mixed on site.

Self levelling concrete shall be performed according to a specific specification.

#### 3.3.1.2	Standards

Following is a list of the main standards concerning this paragraph.

No. of standards		Name of Standards

JUS B.C1.011		Cement – Portland Cement

JUS B.C1.012		Cement – Delivery, Package and Storage

JUS B.B2.010		Aggregate for Concrete

JUS ISO 2736-1		Concrete Tests, Part 1, Sampling of fresh concrete

JUS ISO 2736-2		Concrete Tests, Part 2, Making and Curing

JUS ISO 4012		Concrete – Determination of Compressive strength

JUS U.M1.014		Concrete – Influence of Aggressive Materials

JUS U.M1.016	Concrete – Method of tests for resistance against

freezing

JUS U.M1.045		Transport and delivery of ready mixed concrete

JUS U.M1.048		Concrete – Subsequent testing

JUS U.M1.057		Concrete – Grading of aggregate for concrete

JUS U.M1.058		Concrete – Water for making concrete

JUS ISO 1803		Building Construction - Tolerances

JUS U.M1.035		Form Work for Concrete

JUS U.M1.091		Welded steel with mesh for concrete

JUS U.M1.090		Concrete – Determination of adhesion between 				steels and concrete

ASTM-C-171   (foreign)	Sheet Materials for Curing Concrete.

PBAB 87 			Liquid Membrane – for Curing Concrete

(items 266,267)

DIN 18541-     (foreign)	Thermoplastic Sealing Strips for Sealing

Joints in In-Situ Concrete

BAB 87			Codes of Practice

#### 3.3.1.3	Miscellaneous Items

All the following sections of civil works apply also to this section. (Refer to the Table of Contents)

### 3.3.2	Concrete materials

#### 3.3.2.1	Cement

a)	Type and Quality of Cement

The cement shall meet the requirements of JUS B.C1.011 according to the stated type. In case of no other specifications the cement shall be of the Portland Cement 25 type.

White cement shall meet at least the mechanical requirements for Portland Cement 30 type.

For concrete of MB-50 and above, the cement used shall be Portland Cement 30 type, or stronger.

b)	Supply

The cement shall be supplied packaged by the manufacturer or in bulks. The supply of bulks shall be done in an appropriate container as approved by the Engineer.

Cement supplied in bulks shall be stored in silos with a hermetic closure. It shall not be allowed to be stored in open containers or crates.

Cement supplied in sacks shall be store on the site for the shortest duration possible and the Contractor shall make sure it shall not get wet. Cement containing small lumps, not easily crumbled with the fingers shall not be used, unless tested by the lab and approved. Spilled cement that was gathered shall not be used.

Cement stored for 3 month or more, even if stored as specified, shall not be used, unless approved by the lab after the appropriate tests.

Mixing of the cement from different manufacturers will not be allowed nor mixing of different cement classes from the same manufacturer. The Contractor will require from the supplier of cement to submit a bill of loading as follows:

  - Concrete Manufacturer,

  - Declaration of type and class of cement.

  - Date of clinker grinding,

  - Quantity of cement consignment and relevant information (such as date 	and hour of departure from Cement factory and arrival to site).

#### 3.3.2.2	Aggregates

a)	General

All the aggregates shall be of natural sources and shall meet the requirements of JUS B.B2.010.

At the beginning of construction, the Contractor shall proclaim the source of the aggregates he chooses for the work.

Aggregates used for MB 40 or better or exposed concrete will comply with the codes of practice BAB and standards JUS B.B,2 010.

b)	Aggregates Grading

Aggregates will be screened through standards screens into fractions, and each fraction will be stored in a separate box.

c)	Coarse Aggregates

The coarse aggregates shall be grounded into cubes (if possible). The size shall not be more than one of the following:

  - 1/5 of the minimal size of the form-works.

  - 1/3 of the thickness of the hardened slabs.

  - ¾ of the distance between every reinforcement rods, wires or strand or tensioning cables in the pre-stressed concrete.

  - 25 mm, unless otherwise required in a specific specification.

If not otherwise required, the coarse aggregate shall fit the above mentioned sizes. It shall be on a single grain or multiple grains and shall be chosen according to the grading in the standards for coarse aggregate.

In cases, with prior approval of the Engineer, it shall be permitted not to comply with those specifications, if the methods of spreading and vibrating are such as to permit the use of a different aggregate without the danger of defects such as gravel pockets, hollows etc.

d)	Fine Aggregates

Fine aggregates shall be of natural sources (such as seashore sand, riverbank sands or natural excavations) or ground sands or both.

The aggregates shall comply with the standards for fine aggregates. Ground sands shall be washed.

#### 3.3.2.3	Water

The water for the mixture and for finishing shall be of drinking quality and shall be derived from the drinking pipelines. Water will comply with the standards JUS U.M1.058.

Other water shall be tested by a qualified lab and approved for the use in concrete or in the finishing process, not having bad effects on the quality of the concrete or the reinforced concrete.

#### 3.3.2.4	Admixtures

If not otherwise said, the Contractor may add chemical admixtures, complying with the demands of JUS U.M1.035.

The use of admixtures of the microsilika type shall be permitted if so required in a special specification.

Addition of the Super-plasticizer shall conform to the JUS U.M1.035, according to the type.

The admixtures shall be approved if qualified by an authorized lab that it conforms to the qualifications demanded in the standard, and their effects on other properties of the concrete were taken into account. The amount of the admixtures shall be determined by tests done prior to commence of the structure, taking in account the casting conditions, and the expected climate when casting. The admixtures shall be supplied in the manufacturer’s packaging, in accordance with the JUS U.M1.035, and shall be stored on the site according to the manufacturer’s instructions. It shall be put into the mixer in a method ensuring its exact amount and distribution in the mixture.

The use of air confining admixtures shall be permitted only if the concrete is prepared in good conditions and under supervision according to standards and when there is a constant supervision on the amount of air confined as derived from the primary tests on the site. Air confining admixtures shall not be used in concrete containing coal fly ash.

If using more than one admixture, primary tests shall be performed in certified lab to confirm the compatibility between the admixtures. If it is said in the drawings or the contract documents, that the Contractor shall use any kind of admixture to change certain properties of the concrete, said admixture shall be in compliance with specified requirements.

### 3.3.3	Types and properties of Concrete

#### 3.3.3.1	General

The types of concrete shall be defined according to the concrete properties as demanded in the special specification:

a.	The typical strength according to JUS UM1.015

b.	The maximum grain size of the coarse aggregate.

c.	The consistency.

d.	Control conditions

e.	Special requirements

#### 3.3.3.2	Cement Quantity

The cement quantity shall be determined according to primary performed tests. The minimal amount of cement in reinforced concrete shall be according to standard. Unless otherwise stated in a special specification, the maximum amount of cement for MB-50 concrete shall be no more than 480 kg and for MB-60 concrete – 500 kg.

#### 3.3.3.3	Consistency

The consistency shall be according to the grade in JUS UM8.050. The grading of slump for the concrete, white casting into form-works, shall exceed the grade while shipment to the site, for casting and vibrating.

#### 3.3.3.4	Control Conditions

The control conditions shall comply with the JUS UM8.015.

Concrete of MB-30 quality or better shall be manufactured under good conditions.

Concrete of MB-50, MB-60 or higher strength shall be manufactured under close lab supervision.

### 3.3.4	Manufacturing the Concrete

#### 3.3.4.1	General

The following paragraphs are the requirements for manufacturing:

- Ready mixed concrete (manufactured and distributed by a professional. firm).

- Concrete mixed in-situ.

The more common type shall be ready mixed concrete.

#### 3.3.4.2	Ready mixed concrete

a.   The Plant

The plant where the concrete is brought, shall be certified for mixing concrete under good supervision condition according to relevant standards.

The Contractor shall be responsible for the quality of the concrete.

b.   Distance of the Plant from the Site

Unless otherwise stated in a special specification, the interval time between pouring the mixture into the mixer in the plant and its cast at the site shall not exceed 1.5 hours.

According to that requirement the concrete shall be ordered from a plant which complies with this time limit.

c.    Shipment Certificate

Every shipment shall have a certificate noting at least the followings:

1) Type of concrete according to its strength

2) The concrete fitness to the service conditions – pumping concrete,

exposed concrete etc.

3) The nominal maximum size of the coarse aggregate.

4) Slump grading.

5) The minimal amount of cement.

6) The maximum amount of cement, if required by a special specification.

7) The maximum amount of water in the mixture, if required by a special

specification.

8) Time of adding the water to the mixture.

9) Types of chemical or mineral admixtures (if added).

10) The maximum water amount permitted to add in the site.

d.    Means of Maintaining the Concrete Slump on Site.

In order to get the right grade of slump, as ordered, it is not permitted to add water to the mixture on the site, but the amount approved in writing by the QA of the plant, and written on the certificate. Mixture, thickened to a degree that the permitted allotted amount of water to be added can not bring it back to the right thickness, shall be disqualified and shall not be used. In special cases, according to a qualified lab concession, even if the concrete has thickened as said above, it will be used. The condition is that it can be stirred when it is brought to the site, and a set amount of super-plasticizer admixture can be added, and that it shall be mixed for at least 10 minutes – on the responsibility of the Contractor. Concrete that started to hardened – small lumps started to form – shall not used at any event.

e. 	Organizing the site

The site has to be organized to be able to receive constant flow of incoming trucks loaded with concrete as required. The site shall be organized in a way allowing a quick movement of the trucks to and from the casting site. In order to prevent from the concrete from separating into components, there shall be no need to re-grade the slump for the preplanned means of delivery of the concrete in the site. (For example, troughs with too small a slope and no outlet).

f.	Concrete Supplied By Mixers

The concrete shall not be brought by self propelled mixers to the site if the consistency is smaller than S3, unless prior to shipment the concrete was mixed in a stirring mixer.

#### 3.3.4.3	Concrete Mixed On Site

a)	General

The use of concrete mixed on the site shall have prior approval of the Engineer. The approval shall be submitted only for small amounts of concrete that can not be ordered from the plant as ready mixed concrete and on condition that its strength shall not be above MB-20 and when concrete pump shall not be used for dispersing the mixture. The concrete shall be mixed under medium supervision conditions.  It is not permitted to mix concrete under lesser conditions.

When the Contractor builds a concrete plant on the site, it shall be under the same requirements as for the plants outside the site as prescribed in sub-clause 3.4.4.2 b) above, for approved plants.

b)	Storage of Materials

The aggregates shall be supplied to the site and stored separately, every size under a different storage. They shall be put on a gravel surface or another surface to prevent it from mixing with the soil. The mounds shall be separated by partitions to prevent them from mixing with other aggregates. The heaping shall be done in way to prevent segregation.

Crushed and washed sand shall be heaped on a platform allowing the water to run of out till it has a uniform wetness before using it.

c)	Determining the Proportions for the Mixture

The proportions of the components shall be determined in advance at lab tests, or according to experimental mixture prepared on site or according to mixtures used in other sites where the same type of materials were used on the condition that the Engineer is convinced that the concrete is suitable for use at the site. The mixture shall also comply with the strength requirements for concrete made under medium control conditions. The minimum amount of cement for components that shall be plastered, shall be 280 kg per 1 cum, 300 kg per 1cum for components without plaster. Under any conditions the Contractor shall be responsible for the quality of the concrete.

d)	Dosage and Mixing

Mixing shall be done in a mechanical mixer with capacity for mixing concrete containing at least one bag of cement or weighing the cement with an accuracy of ± 3%. The aggregates shall be weighed or measured by volume with an accuracy of ±5%. Measuring with buckets filled and leveled means complying to those requirements. The water shall be measured by a water gauge mounted on the mixer, with the accuracy of ± 4% or by the use of containers assured of their volume.

A system where the water is running in at the same as it is running out shall not do. The duration of mixing shall be according to the standards. Concrete with a consistency lower than S3 shall be mixed only in a stir mixer.

### 3.3.5	Casting the Concrete

#### 3.3.5.1	General

If required by a special specification or by the Engineer, the Contractor shall submit a schedule for casting. It shall include the description of the equipment used including the reserves.

The Contractor shall notify the Engineer about any casting 24 hours prior to the casting and shall be given the approval to do so at the set date.

#### 3.3.5.2	Preparation for Casting

The casting shall commence after the preparations have been completed, like the formworks, supports etc., including the reinforcements. In case of slopes, the Contractor shall make all preparations needed to get the right angle as shown in the drawings. Before the casting the surfaces of the casting molds shall be wiped clean of all residues wood chips, nails, wires etc. All the equipment shall be checked and made ready for the casting.

The casting shall not be performed if the temperature during the casting and for the next 24 hours shall be lower than 4ºC unless special measures have been taken to protect the concrete from damages caused by the cold or freezing. On days of hot and dry weather, hard blowing winds etc. the casting needs the approval of the Engineer, given in advance. The approval shall be given only after making sure all the necessary arrangements were made to ensure the proper casting in those weather conditions and if those conditions were taken into account when the concrete was prepared, cast and cured.

#### 3.3.5.3	Transporting the Concrete to the Site

The transportation of the ready mixed concrete from the plant to the casting site shall be done in appropriate mixers to ensure that the components shall not segregate or get lost during the transportation. The transportation equipment shall fit conveying without interruptions that might change the concrete slump between the lots. The transportation methods have to be approved in advance.

The transportation mixers and containers shall be wetted before the start of the casting and during it. The concrete shall be transported and cast no later than 10 minutes after it was taken out of the mixer, unless a delay was permitted specially, as for instance in a case of using an admixture, preventing the concrete from hardening (Slump Loss).

Transporting the concrete in open vats shall be permitted only after getting a prior approval from the Engineer and if that fact was taken into consideration when the mixture was prepared. The vats shall be smooth all along with a half circle profile and set at the proper angle to ensure the free flow of the concrete without interference. At the end of each vat there shall be a 60 cm vertical pipe to ensure it shall not segregate.

#### 3.3.5.4	Casting the Concrete

The concrete shall be laid as near as possible to the place of its destination. The method of spreading shall ensure the penetration of the concrete, as it was mixed, into all crevices of the molds, covering the reinforcement rods from all directions, and the segregation of the components shall be eliminated. If the concrete was segregated during the transport, it shall not be used.

Concrete spreading from a higher level than 2 m shall not be permitted unless it is performed with the use of the proper piping and funnels. In places where the concrete might be blocked by rods or molds it shall be necessary to use the proper tools (pipes and funnels) to ensure it flows in a manner that shall eliminate segregation.

Concrete casting into foundations, ramps, on floors and into ordinary beams shall be performed in one continuous operation throughout all their depth. While casting walls, pillars and high beams the concrete shall be laid in horizontal layers of no more than 60 cm thickness.

Concrete that has hardened over the allowed consistency or got mixed with other materials shall not be used.

#### 3.3.5.5	Spreading the Concrete with Pumps

Before starting the casting procedure, the Contractor shall present a plan for conveying the concrete around the site with the pumps.

In case of using a pump the crew shall be briefed and readied to handle the great amounts of concrete pushed by the pumps, spread and vibration compact it.

During spreading, the rubber hose shall be brought as close as possible to the proper place of casting to eliminate the segregation of the components. While casting beams, the concrete shall be laid in layers of no more than 60 cm.

#### 3.3.5.6	Joints

Unless otherwise stated, the concrete shall be spread in the mold in one continuous casting to ensure no joints are formed. The concrete shall be spilled into the mold up to the height set in the drawings.

If undersigned cold joints were created during the casting, they shall be taken care of in such a manner to ensure that the construction strength or function as defined in the drawings shall not be damaged. Handling of the joints created because of unplanned brake during the casting shall be approved by the Engineer.

Unless otherwise stated in the contract documents, the joints shall be treated as follows: the excess cement water shall be taken off before the concrete hardened.

The surface shall be roughened till the gravel shows above the concrete. Before the casting is continued, the surface of the hardened concrete shall be scraped of all foreign materials accumulated on it. The surface shall be cleaned and wetted without excess water. The fresh concrete shall be applied to the joint immediately after it was made wet.

#### 3.3.5.7	Vibrating

The concrete shall be vibrated as soon as it is cast into place, using the tools that shall ensure even and perfect vibration even in the narrowest corners of the structure, around the reinforcement rods and in the corners. The concrete mixture shall fit the vibrating method.

Vibrating shall be done with pin (inner) vibrators of 4-6 cm diameter, with at least 9000 vibrations per second.

Walls that are not thicker than 20 cm can be vibrated with external vibrators placed on the formworks.

There shall be, at least, one spare vibrator of every kind in working condition on the site. The vibrators shall be inserted vertically into the concrete in a distance that shall ensure the vibration of all the concrete.

Concrete with super-plasticizer admixture, as for instance Self Leveling concrete or concrete of S7 slump or higher, shall be compacted manually.

It is not allowed to use vibrators.

The vibrators shall not be used to disperse the concrete to a greater distance than 2 m. The vibration shall be continued till the last of the air bubbles was released, and shall be stopped as soon as cement water appears. When vibrating a new layer, the vibrators shall be inserted into the former layer for a few cm.  Inserting the vibrators and the vibration itself shall be performed with care so as to eliminate the movement of the rods.

#### 3.3.5.8	Concrete Straightening and Smoothing

a)	Horizontal Surfaces

The surface of concrete floors, ceilings and hanging floors, upper surfaces of beams etc. (even if they shall be covered with tiles or other covering) shall be straightened with a hard wood ruler or a metal tool after the concrete was vibrated. Straightening shall go on for as long as the concrete is still plastic. If a crack appears after straightening, the concrete shall have to be compacted and the cracks closed with a metal tool.

Determining the thickness of the concrete layer shall be performed with a solid ruler (taking in account the required slope).

b)	Surfaces as Base for Sealing Surface

Surfaces that shall be covered with sealing sheets shall, in addition to the above said, be smoothened with a “helicopter” after the cement water evaporated, till the surface conforms to the requirements. In locations that cannot be reached with the “helicopter”, the surface shall be smoothened with a metal tool. In case it is needed, it is allowed to spread a mixture of cement with aggregate as described in the clause “Insertion methods” in paragraph below – Concrete surfaces. It is not allowed to spray water or disperse pure cement to make smoothening easier.

If there is need for a special smoothening along with hardening, using the “helicopter”, it shall be done, unless otherwise instructed, as described in the clause “Even laying” in below paragraph.

### 3.3.6	Concrete Finishing and Curing

#### 3.3.6.1	General

The concrete shall be protected from drying from the end of the finish operations and up to the end of the curing. The finishing process shall start as soon as the casting was finished and shall last for at least 7 days, when the cement used is of the regular Portland kind. When using the Quick Hardening Portland Cement, it is possible to shorten the time to 5 days, if so approved by the Engineer.

If part of the building was not finished according to the requirements, that part shall be considered not complying with the requirements and shall be dealt with according to the clause 3.4.9 below.

#### 3.3.6.2	Curing Horizontal Concrete Surfaces

The period for curing horizontal concrete surfaces contains two stages: primary and continuous curing.

a)   Primary curing

Primary curing is intended to prevent “plastic cracking” and damages to the surface of wet concrete. It shall be started as soon as the finishing procedures are completed and the sheen of water is gone from the surface of floors, beams etc. and shall be ended after a few hours. It shall eliminate drying of the concrete by wind or sun.

Primary finish shall be done in one of the following methods:

	Spreading Polyethylene sheets or sheets of geotechnical fabric sheets covered with Polyethylene, meeting the requirements of the ASTM-C-171, on the concrete surface.

	Wetting the concrete with water, sprinkled it as fog through fitting apertures, in a way ensuring the concrete surface shall stay wet without causing any mechanical damage.

Spreading curing materials shall comply with the requirements of ASTM-C-309.  The amount of material shall be according to the standard and according to the manufacturer’s instructions but not less than used on the specimens taken for tests. This method shall not be used in places where the surface of the concrete shall serve as work surface or when the surface shall be the base for a finishing layer (mosaic etc.).

In case of temperature lower than 8-10ºC special protection should carried out as describe in sub-clause 3.4.6.5 below.

b. Continuous Curing

From the end of the primary curing and till the end of the curing period, the concrete shall be kept wet, using one of the methods mentioned above. Alternatively, it is possible to wet the surface of the concrete with constant sprinkling, using sprinklers or pierced irrigation pipes, cover the concrete with a layer of wet sand, 5 cm thick, or cover the concrete with water.

Discontinuous wetting shall not be permitted (as wetting with a hose a few times a day).

#### 3.3.6.3	Curing Surfaces Cast in Formworks

In elements cast in formworks (walls etc.), the ties between the formworks shall be loosened as soon as possible according standard and water shall be spread several times a day on the gap between the formworks and the concrete.

After dismantling the formworks, the concrete surface shall be kept wet by constant water spraying. Alternatively a special curing compound, complying with the requirements of ASTM-C-309 shall be spread immediately after dismantling the formworks, or covering with fabric covered with polyethylene sheets complying with the demands of ASTM-C-171.

For concrete covered with plaster or the like, spraying curing compound shall not be used.

If curing for the needed period can not be processed, the formworks shall stay untouched for longer period than stated in clause3.4.7 below.

In case of temperature lower than 8-10ºC special protection should carried out as describe in clause 3.4.6.5 below.

#### 3.3.6.4	Quick Curing

Under special permission from the Engineer, it shall be possible to use a quick finish method (e.g. heating) but only after that method was approved by a certified lab that the method meets that purpose.

The quick curing method shall make sure the concrete retains its properties when the formworks are dismantled and while loading as designed and as demanded in standards.

The method shall make sure that no damage shall be done to the building. The method shall also ensure that the texture of the concrete and the covering of the reinforcement shall not be damaged and that it shall not cause cracks due to temperature difference or by “thermal shock” during dismantling the formworks.

Quick curing shall be performed under close supervision, according to relevant standard. Even when using the quick curing method, the regular curing methods shall be used after the formworks were dismantled, and the concrete shall be kept wet for at least 4 days after casting, as mentioned before, unless the temperature is under 8-10ºC , and special protection should carried out (sub-clause 3.4.6.5 ).

#### 3.3.6.5	Production and Treatment of concrete in special conditions

Production , transport and placing of the concrete at surface temperatures under 5ºC or over 30ºC is considered concreting in special conditions, which require special protection measures of concrete.

For concreting at temperatures fewer than 5ºC, all production, transport and placing material will be prepared beforehand. The use of frozen concrete will not be allowed.

Cement will be highly active with low consistency and fast release of heat. Cement with added Pozzolana should not be used. Concrete admixtures are subject to prior consent by the Engineer.

Concrete  will be adequately protected immediately after its placing and surface forming, until the concrete reaches 50% of required hardness, while concrete which will be exposed to frost , must attain the required hardness prior to freezing.

In case the forms and heat protection are removed at low temperature, the concrete surface will be protected in order to prevent abrupt cooling of concrete.

The temperature of fresh concrete will range within minimum 8-10ºC, by heating water and admixtures. When water is heated, cement will be put into the mixer after water.

Concreting can be carried out only on surfaces with above 0ºC temperature. If that is not the case, the surface can be heated to 30cm of depth by air, with temperature not exceeding 90ºC.

Special protection measures will also be taken for concreting at temperatures above 30ºC. In addition to the 28ºC limit temperature of fresh concrete from the mixer, the vehicles, formwork and slab surfaces shall be adequately protected against heating of concrete.

Production and placing of concrete under special conditions will comply with the Codes of Practice BAB87 Item 261.

### 3.3.7	Formworks

#### 3.3.7.1	General

The formworks shall be designed, carried out and dismantled according to the requirements of standard BAB 87 and according to the requirements in the drawings and in the special specification. The Contractor shall be the only one responsible for the strength of the formworks and their stability during all the phases of work and dismantling, the time of dismantling and its effect on the cast elements.

The design and mounting of the formworks shall ensure the following:

a)	Bearing all the loads that shall appear during the casting work and till the

formworks are dismantled and lowering them safely to ground or to other parts of the building, if they have enough bearing strength to carry the loads without deformation.

b)	Maintaining the measurements as shown in the drawings for the cast part of the building, within the allowed tolerances.

c)	The plainness of the concrete, the slopes, when needed, and allowed deformation of the formworks during casting.

d)	The finish of concrete surface, the corners, the bulges and the sockets according to drawings.

e)	The formworks shall be sealed to prevent running off of the cement water

While the concrete is being vibrated and designed that no damage be caused  to the concrete, in particular on the corners and the edges, caused by the  changes of volume or when dismantling the formworks.

f)	Dismantling the formworks without causing any damage or tremors to the concrete while it is hardening.

Requirements for formworks for special building shall be specified in a specific specification.

#### 3.3.7.2	Designing Formworks

Formworks shall be designed according to the required concrete shapes including levels, bends etc. Casting of bent or sloped components shall be performed on formworks from the lower part of the component or from both sides. If sloped formworks shall be cast from both sides, the upper ones shall be ready to be mounted but that shall be done according to the stages of the casting.

The formworks design shall include all recesses, openings, holes and grooves etc. and the pipes and sleeves for the different accessories, according to the drawings or as needed for the building performance, shall be placed in them before casting.

Truncation of the edges shall be done with wood, metal or plastic rulers that shall be set to fit the drawings.

At the bottom of the formworks for casting pillars, high walls etc. there shall be a small space left to allow cleaning of the base before casting. Cleaning shall include removal of wood chips and other stuff.

#### 3.3.7.3	Covering Formworks made of Wooden Boards or Plywood

The cover of the formworks as described in BAB 87, is the surface that shall be in contact with the concrete.

If there shall be no other requirement, the thickness of the boards or the plywood shall be at least 21 mm. The width of the boards shall not be more than 15 cm. The boards shall not be planed, but they have to be clean. Plywood shall meet the requirements in standard. If the boards are to be reused, all the concrete residues shall be cleaned and all nails removed. Cleaning shall be done with the appropriate emulsion, or with a commercial mixture approved by the Engineer.

In special cases, as the use of pre - manufactured formworks (wooden formworks with special frames), the Engineer may permit the use of boards and plywood of lesser thickness. Defects in the cover of the formworks shall be mended by changing the boards or by placing wooden rulers between the boards, plastic caulking, covering the places with metal sheets etc. Paper shall not be used for that purpose. The boards shall be adjacent to each other, and if a space of 3 mm or more was found, it shall be plugged before casting.

#### 3.3.7.4	Steel Formworks

Steel formworks shall be approved by the Engineer. The approval shall be given after he was convinced that the steel of the formworks, the thickness and structure are suitable for a large number of castings.

Before the formworks are to be reused, they shall be treated as mentioned in

sub-clause 3.4.7.2.

#### 3.3.7.5	Binding Formworks

The gap between vertical formworks and the walls, beams etc, shall keep only with steel accessories. Wood shall not be used for that purpose. Formworks for walls in contact with water or the ground shall not be tied with steel wires (including galvanized steel). Tying shall be done with special screws or other steel accessories that shall be approved by the Engineer. In any case, the accessory left in the wall shall not damage the impermeability of the wall and it shall be possible to cut the accessory to the depth of at least 30 mm from the surface of the wall. Immediately after the removal of the formworks, the holes shall be filled in with cement enriched with a polymer, intended for that purpose, of the composition recommended by the cement manufacturer.

If the formworks are tied with wires, the wires shall be cut immediately after removal of the formworks. The ends of the wires shall be cut to the depth of at least 20 mm and covered as mentioned above. In places where formworks were fixed by screws, or in any other manner, the holes shall be filled in as mentioned above.

#### 3.3.7.6	Placing Accessories in the Concrete

The size and placement of accessories (for sanitation or electricity accessories, pipes, sleeves etc.) shall be according to the drawings. Accessories not on the plan shall not be put in to the concrete, unless approved by the Engineer.

Unless otherwise mentioned, the concrete covering those accessories shall be at least 5 cm thick and shall ensure continuity of the reinforcement, the loops and the coverings. Stripes fixed to the formworks in order to create grooves for electrical appliances or for other purposes, shall be made of a material that shall not blot when absorbing water (wood shall have to be impermeable), shaped as a trapeze and easy to extract from the concrete.

Chiseling the concrete shall be done only after it was approved by the Engineer. If the needed niches, grooves, holes etc. were not done during the casting, the Contractor shall cut them with the appropriate tools, as approved by the Engineer.

#### 3.3.7.7	Dismantling Formworks

The order of the dismantling and the timing shall meet the requirements in BAB 87. According to the standard, there are two possibilities of setting the timing for the dismantling of the formworks and supporting beams:

  - Without close supervision.

  - With close supervision of the casting stages, the curing and the developing strengths of the concrete.

Special requirements for the order and timing of the dismantling shall be specified in the special specification.

Formworks shall be dismantled only after the Engineer approval. The order of the dismantling the formworks shall be determined in a way to ensure there shall be no load conditions endangering building, or deformations because of crawling and shriveling of the concrete.

Formworks shall not be dismantled of any part of the building, till the concrete is hardened and only if the remaining of the formworks and the support beams, with the aid of the hardened part of the building can carry the load of the building and all the loads that can be put on the building. Dismantling shall be performed with gradual release of the wedges or any other strengthening accessories, so as to avoid causing any damage to the concrete. The timing of the dismantling shall be set to avoid causing any damage to the concrete surface, edges, corners etc. and no deflection.

Immediately after dismantling the formworks, all the wires shall be cut off as said in sub-clause 3.4.7.3.

### 3.3.8	Steel Reinforcement

#### 3.3.8.1	General

The reinforcement steel supplied to the site shall be as required in the drawings, new and meeting the requirements of Israeli Standards, to the specific standard accordingly. The steel shall be stored on the site in separate hips, smooth rods, improved bonding rods, nets etc.

The steel rod shall be free of peeling rust.

The requirements for earthing steel bars etc., shall be as stated in the drawings and the specific specifications.

If there shall be a need for reinforcement steel rods for lightning protection system that shall be performed, unless otherwise mentioned, according to the specifications in the paragraph “Lightning Protection Systems”

#### 3.3.8.2	Reinforcement Preparation

The steel shall be prepared and bent according to the measures in the drawings.

Bending shall be performed without heat, and shall comply with the requirements in the Concrete Regulation, BAB 87.

Steel rods and nets for the reinforcement of concrete that were cut and bent in advance in the factory, shall comply with the requirements in the specification of the Standard Institute Specification.

#### 3.3.8.3	Installation of Reinforcement

Reinforcement shall be installed in the formworks according to the drawings and the requirements of the concrete regulation. The reinforcement shall be tied down and placed on concrete or hard plastic spacers, approved by the Engineer. The spacers and tying shall ensure that the reinforcement shall not move or sink before and during the casting.

Reinforcement rods that were put in across direction to each other shall be tied together at the crossings points alternately, with a wire. The rods in the beams and columns shall be tied to all the hoops and the whole complex shall be place in the formworks and supported with spacers to ensure that it shall not be moved during the casting.

The spacers to be used shall be of industrial manufactured kind, and shall fit the covering above the reinforcement. The spacers shall be made of a material withstanding the alkaline compounds, non-corrosive, and not causing corrosion to the reinforcement rods. The spacer measures shall not deviate from the nominal measures by more than ±1 mm.

#### 3.3.8.4	Lengthening the Rods

The rods shall be connected only as shown in the drawings. The lengthening method shall comply with the requirements in BAB 87.

#### 3.3.8.5	Clearance between the Rods

The clearance between parallel rods shall allow for easy casting and insertion of the vibrators. The clearance, if not otherwise said in the drawings or any other contract documents, shall be as stated in BAB 87 at least.

#### 3.3.8.6	Cover Thickness

Unless otherwise mentioned, the thickness of the covering layer of concrete above the reinforcement shall be at least as required in the BAB 87. The Contractor shall make sure the thickness shall comply with sub-clause 3.4.8.3.

#### 3.3.8.7	Reinforcement of Joints

If spikes are to be inserted into the foundations of the columns or the piles, their diameter, length and quantity shall be as shown in the drawings. If the reinforcement of the columns is inserted into the foundations, at least 2 hoops shall be placed in the foundation.

At the overlapping area it shall be made sure that the covering layer shall be as required.

Spikes shall be set, according to the drawings, in places where a bonding of the components of the building have to be bonded after being cast at different times. The protruding spikes, of the finished components, shall be cleaned from all the residues of the former casting before continuing with the casting.

### 3.3.9	Quality Assurance

#### 3.3.9.1	General

The QA specifications shall apply to manufacturing of the concrete, the characteristics of wet and hardened concrete and the characteristics of all the components.

#### 3.3.9.2	Controlling the Concrete Manufacturing

The ready mixed concrete shall comply with the relevant standard, and to the requirements of the contract document.

The plant supplying the concrete shall comply with the requirements in sub-clause 3.4.4.2. The concrete mixed at the site shall comply with the requirements in sub-clause 3.4.4.3.

#### 3.3.9.3	Strength in Pressure Test

For testing the concrete, from any source, specimens shall be taken from fresh concrete and shaped into cubes. Those cubes shall be tested 28 days later, unless otherwise said in the contract documents. The methods for sampling, their shape, and testing shall comply with the JUS UM1.048. If for some reason no specimens were taken from fresh concrete, the Engineer can order for specimens to be taken from the hardened concrete and testing them according to the JUS UM1.049. Sampling and testing shall be done within 60 days after casting.

The Engineer shall determine which of the components shall be sampled according to the requirements above.

Specimen from concrete processed through a quick curing process, shall be tested under the same curing methods and conditions (temp., wetting etc.) instead of the regular curing method. Specimens shall be taken and tested before dismantling the formworks and also at the age of 28 days.

If so required by the Engineer, some samples shall be taken out from the concrete (according to JUS UM1.049) of the elements processed through a quick curing process to verify the tests results. If there is a doubt as to quality of the curing process, the Engineer may demand to sample the concrete again.

#### 3.3.9.4	Complying With the Requirements

a)	Strength requirements

The concrete shall comply to the requirements for average pressure strength (f c) and the pressure strength of any specimen (f ci) as defined in the BAB 87 for that type of concrete.

If the concrete does not comply with one of the requirements of the BAB 87 for strength of a specimen taken from fresh concrete at the age of 28 days, the Engineer shall permit sampling cylinders to be taken from that element, providing that the tests shall be executed within 60 days. The cylinders shall be taken and tested according to the JUS UM1.049. If the cylinder specimens do not meet the required results, the whole element in question shall be considered defective and shall be dealt with in one of the following ways, according to the Engineer opinion:

a1.	The Engineer shall disqualify the element and the Contractor shall demolish that part and rebuild it.

a2. The Engineer shall accept the defective concrete under specific conditions, and shall reduce its cost accordingly.

b)	Strengthening a Component made of Defective Concrete

If the Engineer agrees to accept the defective concrete component but required that it shall be strengthened, the strengthening method shall be subject to the Engineer’s approval.

c)	Tolerance

Tolerance is the deviation of the actual measures from the nominal. The required tolerance grade shall be as mentioned in the drawings or in the contract documents.

The permitted deviations shall be in according to requirements in the standards JUS ISO 3443-1 -ISO 3443-6.

Element that do not comply with the tolerance requirements might be disqualified.

d)	Testing the Thickness of the Concrete Cover over the Reinforcement

If there is a suspicion that the cover over the steel reinforcement does not comply with the requirements, including the tolerance, and there is no requirement in standards, the Engineer may demand to test the thickness of the cover layer in a nondestructive method. The test shall be done by mapping the thickness of the cover layer of that component, with a special tool and by a qualified lab.

The tested component shall be considered in compliance with the requirements, if the average of the cover layer and the cover of the separate rods, comply with the requirements.

e)	Testing the Effectiveness of Curing

If there is a suspicion that curing of the element was not executed according to the requirements, the Engineer can demand a test, destructive or nondestructive, to be conducted by a qualified lab.

f)	Sealant Requirements

If the requirements include sealing of the building against water under pressure, the concrete shall comply to the requirements in Section 3.8.

Building that are under water pressure, like basements shelters and water pools shall be tested and qualified according to a special specification.

#### 3.3.9.5	Concrete Repairs

For concrete that was not categorized as exposed, all the defective surfaces shall be repaired– as for instance filling in cracks and gravel pockets, removing bulges etc. as approved by the Engineer. Such repairs shall not be made in cases the defect reaches the reinforcement. In those cases the repair shall be executed according to a special specification.

The Engineer can permit repair of the exposed concrete, but that permission shall not hinder him from ordering the element to be demolished, if the repair does not match the quality of the sample panel (decorative exposed concrete). The Contractor shall not start repairs until the concrete tests were run and the Engineer approved them.

If after dismantling the formworks and the concrete tests, defects like aggregate pockets, holes etc. were revealed, creating a flaw in the exposed concrete but do not penetrate to the reinforcements, the Engineer can authorize the following repair procedure:

The Engineer will mark the areas to be repaired and those shall be chiseled out vertically to the surface. The chiseled area and 15 cm around it the concrete shall be wetted.

All the area shall be brushed meticulously with cement mixture, as thick as thick paint, with additional polymer emulsion to improve bonding. The ratio of the mixture shall be according to the manufacturer’s instructions. After that the hollow is filled in and dense with a concrete mixture similar to the original one, but without coarse aggregate. On decorative surfaces, part of the cement shall be replaced with white cement to improve color. The shade of the filling shall be tested in advance by experimental filling let to dry. The filling shall protrude a little from the surface, and after 1-2 hours it shall be straightened with a wooden strengthener. Curing shall be meticulous on the surface of the concrete and on the repaired surface as well. Repair of joints, formworks crevices etc. shall be applied thus that the appearance of the surface shall be exactly as it shows in the drawings. The holes left after the formworks connectors were removed and other such holes shall be filled in with cement mixture as mentioned above, after the area was wetted.

#### 3.3.9.6	Disqualifying Elements of the Building

Building parts rejected according to the tests results, for deviations larger than permitted (including reinforcement cover thickness) or because of defective curing, not complying with the water resistance requirements, or any other defect that reduces the stability or the duration of the building, the elements cast from that concrete shall be demolished and recast by the Contractor.

In addition to clause A – exposed concrete with a defective surface or with

cracks, or that the surfaces deviate from the drawings, or that the joints do not fit the drawings , or that the surface does not match the specimens etc. – shall be considered as concrete not complying with the requirements. The Contractor shall demolish those elements and shall recast them.

If the Engineer agreed with the repairs suggested by the Contractor, or the repair or strengthening of a disqualified element is required, after detecting one of the above mentioned defects, the Contractor shall bear all the expenses for that work. The method shall always be subject to the approval of the Engineer.

## 3.4	Water lines – construction works

### 3.4.1	Surveying works

Pipeline route marking and as-built surveying

Before beginning of pipe laying works it is necessary to mark the route by establishing benchmarks along the route. Upon works completion, as built situation is to be recorded by licensed institution.

It is also required to record and create a cadastre of underground installations containing all underground installations and structures en route, or at the concerned location. Upon the works completion the Contractor should submit the confirmation of execution of as built surveying, issued by an authorized institution.

Payment of works is by m’ of marked or surveyed pipeline.

### 3.4.2	Earthworks

#### 3.4.2.1	Machine excavation of trenches

Machine excavation should be carried out either by temporary disposal of excavated soil at a minimum distance of 1.0 m from the trench, or by direct loading to a transportation vehicle for landfill disposal. Machine excavation should be carried out up to 0.2m from the designed trench bottom, in accordance with longitudinal profiles and cross sections. The trench width and depth should be in accordance with the design.

At pipeline sections through agricultural areas it is required to temporarily remove and dispose a humus layer of defined thickness. Upon trench backfilling, humus layer is reinstated.

Trench excavation shall be carried out with vertical trench sides, which should be secured. All excavation should be carried out in accordance with the design, and elevations should be verified in writing, in a construction log, by the Engineer. Inaccurate excavation shall not be accepted, and should be remedied by compacted gravel, or by pouring of mass concrete, as directed by the Engineer. If the Contractor encounters unknown underground installations or structures, or soil composition is different than expected, appropriate safety measures should be introduced immediately, and the Contractor should seek further instructions.

Trench sides shall be adequately supported, shored, or safely battered back at all times.

Unless otherwise specified, shown on the drawings, or directed by the Engineer trenches for pipelines shall be excavated to the following limits:

Width	: (at crown of pipe)

    - Minimum:

      - External diameter plus 400mm

      - No trench to be less than 600mm wide

    - Maximum:

      - External pipe diameter plus 600mm.

In rock, greater widths may be allowed by the Engineer at the Contractor's own expense.

Sufficient width shall be allowed at pipe joints to give adequate room for jointing operations.

Depth: Except where the pipeline is graded to specified levels as shown on the Drawings, the minimum trench depth shall be such that the minimum cover on the pipes measured from original ground level to the top of the pipe barrel shall be 1,200mm in roads adjacent margins and paved areas, and 900mm otherwise.

Allowance shall be made in the trench depth for the required thickness of pipe bedding material over the full trench width.

Trenches shall be excavated to the widths shown on the relevant drawing or as may be specified in any particular case.  Maximum widths shall not be exceeded without the express approval of the Engineer.

Excavated soil that is going to be used for backfilling should be cleaned from all stones larger than 20mm, roots and large turfs.

During excavation works all necessary measures of safety at work should be undertaken, as well as excavation protection during elements. Quantities of excavation shall be calculated in accordance with the real status, or as approved by the Engineer.

Payment for works shall be by m3 of excavated material.

#### 3.4.2.2	Manual trench excavation

Manual excavation is carried out:

- Starting from 0.2m from the designed trench elevation

- At intersections with underground installations

- At sections where machine excavation is not possible

Manual excavation should be carried out in accordance with the design, and elevations should be verified in writing, in a construction log, by the Engineer. Trench excavation shall be carried out with vertical trench sides, which should be secured. Trench width and depth should fully comply with the design. Excavated soil that is going to be used for backfilling should be cleaned from all stones larger than 20mm, roots and large turfs. Excavation with the existing underground installation should be carried out in presence of the authorized of the installations owner.

Manual excavation shall be carried out only in trench properly secured with supports and shuttering.

Quantities of excavation shall be calculated in accordance with the real status, or as approved by the Engineer.

Payment for works shall be by m3 of excavated material.

#### 3.4.2.3	Excavation in Rock

Where rock is met with in excavations as much as possible of it is to be removed by means other than blasting.

The use of explosives for loosening or splitting up hard material will be permitted only with the prior approval of the Engineer.  The manner, times and method of blasting shall be subject to the approval of the Engineer.  Any approval, permission or advice given by the Engineer shall not relieve the Contractor of any of his responsibilities for injury to persons or property.

The Contractor shall comply with all current regulations for the purchase, transport, storage and use of explosives.

Blasting shall be carried out by experienced personnel only and adequate warning shall be given to all persons in the vicinity.

The Contractor shall give adequate notice to the Engineer of his intention to use explosives so that the relevant authorities can be informed.

Explosives shall be used in such a manner as to impart the minimum vibration to the surrounding ground.  Resultant ground wave peak particle velocities shall not exceed 25mm/sec at adjacent structures, pipes etc.  Vibro-graph readings shall be taken to determine the resultant ground wave velocities for all blasts.

The site of the blast shall be adequately covered with blasting mats, heavy timbers etc., to prevent fly rock and all exposed pipelines, services, structures etc., shall be adequately protected from the results of the blast.  Any damage done to structures, services, pipelines etc., shall be immediately repaired by the Contractor at his own expense.  The Contractor shall indemnify the Contracting Authority against any loss or damages caused by his blasting operations.

#### 3.4.2.4	Removal of Faulty Ground

All soft places, faults etc, in the bottom of the excavations and trenches shall be excavated to such depths as may be directed and then filled in with approved material.

#### 3.4.2.5	Over Excavation

Any excavation carried out inadvertently by the Contractor below the required depth for the structure or pipeline shall be filled and compacted with approved material up to the required level, at the Contractor's expense.

#### 3.4.2.6	Protect Existing Buildings

The Contractor shall make all necessary provision for shoring, strutting, underpinning or supporting any walls, foundations or other built structures, the stability of which may possibly be endangered by the execution of the works.

#### 3.4.2.7	Timbering Excavations

The Contractor shall furnish, put in place and maintain such sheeting, bracing etc., as may be required to support the sides and roof of the excavation and to prevent any movement which can in any way injure the masonry, concrete or pipeline, diminish the necessary width of excavation, or otherwise injure or delay the work or endanger adjacent pavements, buildings or other structures.  If the Engineer is of the opinion that at any points sufficient or proper supports have not been provided, he may order additional supports put in at the expense of the Contractor and the compliance with such orders shall not release the Contractor from his responsibility for the sufficiency of such supports. Care shall be taken to prevent voids outside the sheeting, but if voids are formed they shall be immediately filled and consolidated to the satisfaction of the Engineer.

#### 3.4.2.8	Timber Left in Trench

The Contractor shall leave in place to be embedded in the backfill of excavations or tunnels all sheeting, bracing etc., not so shown on the plans which the Supervisor may direct in writing to be left in.

All other sheeting and bracing shall be removed in such a manner as not to endanger the constructed structure, pipeline or properties whether public or private.  All voids left or caused by the withdrawal of sheeting shall be immediately refilled and compacted.

The right of the Engineer to order sheeting and bracing left in place shall not be construed as creating any obligation on his part to issue such orders and the non-exercise of this function shall not relieve the Contractor from liability for damages to persons or property, occurring from or upon the work, occasioned by negligence or otherwise, growing out of the failure on the part of the Contractor to leave in place in the excavations and trench sufficient sheeting and bracing to prevent any caving or moving of the ground adjacent to the banks of the excavations and trench.

#### 3.4.2.9	Dewatering

Where required for the protection of road sub-grade or the subsoil beneath the foundations and pipelines the Contractor shall remove by pumping, baling or otherwise any water, from any source whatever, which may accumulate or be found in the excavations and trenches and other openings made under this contract and shall form all dams, flumes or other works necessary to keep them entirely clear of water while pipelines are being laid and backfilled and foundations, structures and roads are being constructed.  The Contractor shall have at all times upon the works sufficient pumping machinery ready for immediate use.

Water from the trenches and excavations shall be disposed of in such a manner as to avoid damage to roads, public or private property, silting of drains or blocking water courses, the work completed or in progress and it shall not cause unnecessary interference with the use of the roadworks or accessways by the public or become a public health hazard.

#### 3.4.2.10	Removal of Offensive Matter

All filth or other offensive matter met with during the excavation of the works immediately it is encountered shall be moved to a suitable approved dump and shall not be deposited upon the surface of any street, or any place near a dwelling house or where it is likely to be a nuisance.

#### 3.4.2.11	Lay Temporary Drain

Whenever so directed by the Engineer, the Contractor shall excavate a trench or lay a temporary pipeline from the excavations to a natural water course.

#### 3.4.2.12	Backfilling (in normal ground)

Unless otherwise directed all excavations shall be backfilled as soon as the structures therein have acquired adequate strength or pipelines have been laid and tested. Once started backfilling shall be carried out expeditiously.

Excavated material shall be used for backfilling where approved by the Engineer. It shall be laid and compacted in 200mm layers. Compaction shall be by means of six passes of a vibrating-plate compactor or approved equivalent. If the Contractor allows material, which, on excavation, is suitable for re-use to become unsuitable for backfilling he shall replace it with approved material at his own expense.

#### 3.4.2.13	Backfilling (in Rock)

Where the filling material contains broken rock and stones special precautions shall be taken to protect structures or pipelines within the excavations.

Protective sand or granular surround to a minimum depth of 300mm shall be placed over pipelines to the full width of the trench before rock backfill commences.

Backfill of the first 600mm layer of rock or stones shall be carried out carefully and no rock or large stones shall be allowed to protrude into the protective clay layer. The interstices of the rock backfilling shall be filled with smaller stones and clay and the whole compacted carefully.

Any damage caused to structures or pipelines during the backfilling operations shall be rectified at the Contractor's expense.

#### 3.4.2.14	Granular Backfill

Granular backfill shall be crushed rock graded within the following limits and compacted in 225mm layers:

| Sieve Size | Percentage by Weight Passing |
| --- | --- |
| 75 mm | 100 |
| 40 mm | 85-100 |
| 10 mm | 40-70 |
| 5 mm | 25-45 |
| 0.6 mm | 8-22 |
| 0.075 mm | 0-10 |

#### 3.4.2.15	Deficiency of Material for Fill

Should there be a deficiency of suitable material backfilling, the Contractor shall supply and place such additional materials as may be required.

#### 3.4.2.16	Disposal of Surplus

As each excavation and trench is refilled the surplus excavated materials shall be at once removed, the surface having been properly restored to its original level.

#### 3.4.2.17	Grading and compaction of trench bottom

Grading of trench bottom is performed manually with tolerances of ± 1cm, in accordance with designed elevations and grades, with soil disposal next to the trench. Grading is carried out only under protection of trench supports. Trench grading is followed by trench bottom compaction, by means of appropriate mechanical equipment. Compactness must reach minimum 15 MPa. If necessary, the prescribed minimum compactness must be achieved by adding sandy-gravel material.

Payment should be carried out by m2 of graded and compacted trench bottom.

#### 3.4.2.18	Preparation of pipe bedding

Sand for pipe bedding is spread with a tolerance of ±1cm, in accordance with the designed elevations and grades. Bedding thickness is defined in the designed. The price includes bedding material purchase, loading, transportation, distribution along the trench, spreading in the trench, grading and compaction, as required. After compaction is finished bedding loading capacity is to be verified. The minimum compactness should be at least 95% of the maximum laboratory compactness after Proctor. If compactness is checked by examining the module of compression it must be Me > 1.5 kN/cm2.

Payment for works shall be by m3 of compacted bedding.

#### 3.4.2.19	Backfilling with pipe surround

Backfilling with pipe surround material (sandy-gravel with Dmax20mm) is carried up to the elevation defined by the design, or up to the lowest elevation of the road or pavement sub-base. Backfilling with pipe surround is carried out in layers 20-30cm thick, with parallel compaction and watering. Upon trench backfilling backfill bearing capacity should be checked.

Under roads backfill compaction should be up to 100% of the maximum laboratory compaction after Proctor (in accordance with JUS-4 UB1.016). If the examination is carried out by checking the compression module (in accordance with JUS.UB1.046), it should be minimum Me 2.5 kN/m2.

Under paved pedestrian or bicycle paths backfill compaction should be up to 98% of the maximum laboratory compaction after Proctor (in accordance with JUS-4 UB1.016). If the examination is carried out by checking the compression module (in accordance with JUS.UB1.046), it should be minimum Me 2.0 kN/m2.

Payment for works shall be by m3 of compacted pipe surround.

#### 3.4.2.20	Trench backfill with excavated soil

After backfilling with pipe surround is finished, the rest of the trench is backfilled with excavated soil. Backfilling with excavated soil is carried out in layers of 20cm with parallel compaction. Backfill compaction should correspond to the surrounding soil, or should be at least 95% of the maximum laboratory compactness in accordance with the Proctor’s procedure, whichever is greater. Excavated soil for backfilling should not contain large particles, stones and plant roots.

Payment for works shall be by m3 of compacted soil.

#### 3.4.2.21	Transport and disposal of surplus soil

Surplus soil is loaded into trucks, unloaded at a designated, approved local landfill, spread and graded.

Payment for works shall be by m3 of transported and disposed soil.

### 3.4.3	Carpentry works

#### 3.4.3.1	Trench wooden supports

Excavated trench must be secured by appropriate wooden shuttering with corresponding wooden columns and other necessary supports. Vertical columns must be of wood of required quality class, without nodes. For entering and getting out of the trench proper ladder must be used. Excavation must not be carried out in layers more than 20-30cm thick. The trench must not be left unsecured during night, weekends, holidays, etc. The trench supports are removed gradually, as the trench is backfilled. At the beginning of each working shift, the supports must be thoroughly inspected and if necessary repaired. The works can resume only upon the Engineer’s approval.

Payment for works shall be by m2 of supported sides.

#### 3.4.3.2	Trench metal supports

Securing the trench with metal supports is carried out by fixing the supports vertically into the trench bottom. Upper and medium sections of the supports should be additionally secured with horizontal beams, in accordance with the structural calculations of the supports.

Excavation must not be carried out in layers more than 20-30cm thick. The trench must not be left unsecured during night, weekends, holidays, etc. The trench supports are removed gradually, as the trench is backfilled. At the beginning of each working shift, the supports must be thoroughly inspected and if necessary repaired. The works can resume only upon the Engineer’s approval.

Payment for works shall be by m2 of supported sides.

### 3.4.4	Covering and insulation works

All materials used for insulation works should fully comply with corresponding JUS standards (including composition, physical and mechanical properties, form, etc.), and accompanied by appurtenant attests. If some of materials are not specified in JUS standards, the attests should be sought from an authorized institution.

Insulation works must be carried out in accordance with the design, technical specifications and relevant JUS standards and manuals, as well as in accordance with standard engineering practices.

Before execution of insulation works is commenced, all previous civil engineering works that can affect quality, durability and reliability of insulation works must be thoroughly inspected.

Insulation works should be carried out only on good quality surfaces in accordance with the Rulebook on technical measures and specifications for hydro-carbonate insulation of roofs and balconies where properties of different base surfaces are defined. During insulation works all prescribed coats and layers must be applied.

Insulation works should be done in accordance with the detail drawings, and water-tight joints must be established with other insulation materials or structure elements.

During execution of insulation works, or upon their completion, while insulation laysers are not protected, it is forbidden to step on insulation layer, to store other materials or carry out transport over insulation. Only those works can be done in parallel that do not damage placed insulation.

The lowest permissible temperature for placing bituminous materials is +5C. For cold insulation layers, the minimum permissible temperature is +10°C.

Overlaps of insulation sheets must not be less than 10cm. An exception from this rule could be when special joining strips are applied, and insulation sheets are practically welded.

The Contractor must implement all necessary sanitary-technical protection measures, and all staff taking part in insulation works must be informed with the sanitary-protection measures, and must abide to them.

The cost of works includes the following: workmanship, basic and auxiliary materials, transportation, storage, cleaning of the location, removal of excessive materials and debris, any damages caused to other works. The cost also includes all necessary measurements, marking, quality control, obtaining of attests etc.

### 3.4.5	Sheet-metal works

Sheet-metal works must be carried out of good quality, in accordance with the relevant regulations and their properties and dimensions must be in accordance with the relevant JUS standards. If the material is not specified in the JUS standards, an attest must be obtained by an authorized institution.

Galvanized metal-sheets must comply with JUS.C-B4-.O81 and JUS C-E4-020 and copper metal sheets must be in accordance with JUS.C.D4-500 and JUS.C.D4.020.

Auxiliary joining material, such as tin, bolts, and other must comply with the JUS standards. Contact of two different metals must be avoided if it causes corrosion or other harmful effects. Steel elements for fixing of galvanised sheets must also be galvanised, if no other adequate protection is prescribed. Copper sheets must be fixed by using copper braces and supports. Material of bolts must be the same as material of metal sheet.

Joints and fixing must be installed in such a manner so that they can freely expand or shrink depending on temperature variations, and should remain water-tight. Metal sheets must be protected by a bituminous coat against detrimental effects of cement mortar or bricks.

Unit costs include all primary and auxiliary materials, workmanship, temporary scaffolding, transportation and storing of materials, cleaning of workplace, removal and disposal of debris and packaging, repairs of other works. The cost also includes all measurements and applicable OHS measures.

3.4.6	Ironmongery works

All ironmongery works must be carried in accordance with the technical description, bill of materials, detail drawings and instructions in the design. Materials used must be in accordance with applicable JUS standards, and in case the material is not specified in JUS, an official attest must be provided.

Installed ironmongery elements must satisfy the following requirements (as required):

- Air-tightness

- Water-tightness

- Transparency

- Ventilation

- Thermal insulation

- Sound protection

Also, ironmongery elements must be durable, functional, safe for usage and if applicable fire-resistant. Elements must be installed so that they are not affected by temperature changes. Before the works, the Contractor should specify joining methodology, type and form of locks, method of glazing (if applicable), fixing of elements (welding, anchoring, etc.).

If different materials are to be in contact, that should not effect in corrosion, or other detrimental effects. When fixing the elements to concrete or brick walls materials that can damage the element must not be used (gypsum and other). Where required, surfaces must be protected against corrosion.

Unit costs include all primary and auxiliary materials, jointing materials (anchors, bolts, etc.) workmanship, temporary scaffolding, transportation and storing of materials, cleaning of workplace, removal and disposal of debris and packaging, repairs of other works. The cost also includes all measurements and applicable OHS measures.

When calculating material quantities a provision of additional 7% must be added for jointing elements and protection layer.

### 3.4.7	Hydraulic testing of pipeline

#### 3.4.7.1	Pressure testing of pipeline

All installed pipeline must be exposed to pressure tests. Main purpose of these tests is to establish water-tightness of a pipeline and its stability. It should be noted that certain pipe materials adsorb water to a certain extent. Water-tightness of the pipeline is checked by introducing pressurized water. The testing procedure should be conducted in accordance with the manufacturer’s manuals, and generally includes the following:

- Filling the pipeline

- Preliminary test

- Main test

- Control examination

- Final test

- Rinsing and disinfection of the pipeline

Pipeline testing is carried out per sections which should be 300 to 500m long. If testing sections have not been identified in the design, this should be done by the Engineer, taking into account the pipeline length, works and backfilling schedule. Before testing, pipeline must be backfilled with layer of 30 to 50cm. Joints must be free and accessible. Section ends must be supported, so that any axial movement is prevented. These supports can be removed upon test completion and when the pipeline is fully de-pressurized. For safety reasons, staff must not stay in the vicinity of the supports during testing.

#### 3.4.7.2	Pipeline filling and air evacuation

Upon pipeline setting for tests, the pipeline is filled with water which must comply with the potable water regulations. The pipeline is filled gradually in order to ensure proper air evacuation. The pipeline is filled from its lowest point, preferably with flowrate that effects in the average velocity of 0.5m/s. It is necessary in install an air valve or hydrant to enable air evacuation. The following table defines required flowrates for filling of different pipe sizes.

|  (mm) | 40 | 50 | 65 | 80 | 100 | 150 | 200 | 250 | 300 | 400 | 500 | 600 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Q (l/s) | 0.1 | 0.1 | 0,15 | 0.2 | 0.3 | 0.7 | 1.5 | 2.0 | 3.0 | 6.0 | 9.0 | 14.0 |

Before the test commences, it should be checked whether air is fully evacuated.

#### 3.4.7.3	Pre-testing

Pre-testing is carried out in order to check water-tightness of joints.

- For steel and ductile-iron pipes pre-tests are carried with the maximal operational pressure

Pre-test duration depends of pipeline diameter:

  -  150 mm			-	0.5h per 100m of pipeline

  -  200 -  400mm       	-	6 h

  -  450 -  700mm      	-	12 h

  -  > 700mm			-	24 h

- uPVC pipes should be pre-tested for 12h

- For PN10 pipes	-	test pressure is15 bar

- For PN15 pipes 	- 	test pressure is 21 bar

- For HDPE pre-test is carried out with test pressure of 15 bar for PN10 pipes. Because HDPE is affected by temperature changes, pipe wall temperature during tests must not be above19°C. Pre-test duration for HDPE pipelines with joints lasts 12h, and if the pipeline has no joints, 4h.

If pre-testing shows that certain pipe sections or joints are not water-tight, pressure should be increased up to normal test pressure, in order to clearly identify all weak points. Corresponding pipe repairs should be followed, but only when the pipeline is fully de-pressurized.

#### 3.4.7.4	Main testing

Main testing is carried out upon completion of the pre-testing. Generally, test pressure for the main testing equals the maximum working pressure multiplied by 1.5.

  - For cast-iron and steel pipes test pressure should be by 5bar higher than the maximum working pressure, but not less than 10bar.

  - For uPVC pipes main testing lasts 3h, as follows:

    - For PN10 pipes	-	test pressure is 15bar

    - For PN16 pipes	-	test pressure should be 21bar

  - For HDPE pipes main testing lasts 3h, and for PN10 pipes, test pressure is 13bar.

Test pressure in the pipeline should be as specified at the highest point along the pipeline route. All joints, thrust blocks should be thoroughly examined, and any deformation identified. Preferably, temperature during testing should be fairly constant.

The main testing duration should be as specified:

- For steel and cast iron pipelines:

    - 150mm 		-	0.5h per each 100m of pipeline

    - 200 - 400mm	-	6h

    - 450 - 700mm      	-	12h

    -  > 700mm		-	24h

Note: Exceptionally, the main testing duration can be reduced, as approved by the Engineer. Under no circumstances should the aforesaid testing pressures be increased.

#### 3.4.7.5	Control testing

Upon completion of the main testing, joints are covered with soil layer of 30-50cm. During the control testing, test pressure is equal to working pressure for steel and cast-iron pipelines. Pressure recording is performed by a calibrated pressure meter. The pressure meter scale should have 0.1m intervals. Two pressure meters should be installed, at the lowest and at the highest point on the pipeline. The pipeline passes the test if pressure drop is less than 0.1 bar.

The test results should be recorded in writing. The test report should be signed by the Investor and by the Contractor. This procedure is compliant with DIN and JUS norms.

Predstavnik Investitora mora da prisustvuje  ispitivanju  cevovoda i obezbedi kontrolu

### 3.4.8	Pipeline disinfection

In order to remove dirt and fine particles in the pipeline, it should be rinsed, and then disinfected. Proper rinsing is essential for successful disinfection.

#### 3.4.8.1	Pipeline rinsing

Only water of potable quality can be used for pipeline rinsing. Effective rinsing is achieved only if the mean velocity in the pipeline is > 1.5 m/s. Washouts on the pipeline are normally used for rinsing, from higher towards lower points.

Rinsing water discharge should not cause any damage in a washout zone. Proper protection of the washout zone should be established on site, as approved by the Engineer.

Volume of water required for pipeline rinsing:

- For  < 150mm	- internal pipe volume x 3-5

- For  > 150mm 	- internal pipe volume x 2-3

Rinsing is carried out until clear water appears at the washout.

#### 3.4.8.2	Pipeline disinfection

Disinfecting agent should be prescribed by a sanitary department of a local PUC, and approved by a local municipality sanitary department. Disinfection control is performed by an authorized representative of the PUC sanitary department.

Chlorine concentration in water during disinfection should range between 10 and 200 mg/l (normally between 30 and 50 mg/l). Exact concentration is determined by the representative of the sanitary department of the PUC.

Lower concentrations (10 mg/l) can be allowed  if a contact time is 12 t0 24 hours. Normal contact time is 3 to 12 hours.

The minimal contact time is 30 to 60 minutes. Chlorine injection can be performed through a hydrant or designated connection. During disinfection, parts of a distribution network in normal operation should be separated from the pipelines that are being disinfected. It is very important to apply necessary OHS measures, because chlorine is considered to be very dangerous chemical, and risky for human health. Also carrying out of the disinfection should be publically announced by the authorized PUC representative in order to avoid any risk of the pipeline being used. A report must be prepared on disinfection procedure, and verified by the authorized representative.

APPENDICES TO CHAPTER A:

Civil Works

### General

- All materials and goods shall be manufactured/tested/supplied in accordance with recognized, approved, Serbian or international Standards.

- The Standards mentioned in the appendices will be approved against the relevant section and/or item and give a guide as to quality requirements.  The use of alternative, equivalent or superior Standards proposed by the Contractor in accordance with the Specification, subject to Engineers approval, will be permitted.

- Reference to any Standard means reference of all associated or related Standards referred to within that Standard.

- The appendices include reference to publications for guidance on current practice on some subjects.

- The editions of approved Standards used shall be those current 28 days before the date for the return of Tenders.

- The Contractor may be required to supply any of the Standards or publications listed in the appendices for the use of the Engineer, if required (with English language translations).

- The British Standards referred to have been issued by the British Standards Institution, 2 Park Street, London WIA 2BS.

- The DIN Standards referred to have been issued by the Deutches Institute für Normung, 10772 Berlin, Germany.

- The ISO Standards referred to have been issued by the International Organisation for Standards, 1 rue de Varembé, Case Postale 56, CH-1211 Geneva, Switzerland.

- The ANSI Standards referred to have been issued by the American National Standards Institute, 1819 L Street NW, Washington DC 20036, USA.

- The ASTM Standards referred to are obtainable through the ANSI.

- The AWWA Standards referred to have been issued by the American Water Works Association, 6666W, Quincy Avenue, Denver CO 80235, USA.

- The API Standards referred to have been issued by the American petroleum Institute, 1220 L Street, NW Washington DC 20005-4070, USA.

- The Serbian standards referred to have been issued by Serbian standards institutions.

- A list of Serbian regulations regarding Construction Works, that form part of the Contract, is given in Appendix 1 A.

### APPENDIX 1:  List of Serbian Standards and Regulations

A.	GENERAL LEGAL REGULATIONS

- Planning and construction law; Official Gazette RS No. 47/2003

- Standardization law; Official Gazette SFRJ No. 37/1988, 23/1991 and 55/1991

- Obligation law; Official Gazette SFRJ No. 29/1978, 39/1985, 45/1989, 57/1989 and 31/1993

- Special construction usances; Official Gazette SFRJ No. 18/1977 and 29/1978

- Law on protection at work; Official Gazette RS No. 42/1991, 53/1993,67/1993,48/1994 and 42/1998

- Regulations on measures and procedures of construction supervision; Official Gazette RS No. 105/2003

- Regulations on technical control of objects of investment; Official Gazette SRS No. 9/1969

- Regulations on protection at work during construction; Official Gazette RS No. 53/1997

- Regulations on measures and standards of protection at work with working tools; Official Gazette SFRJ No. 18/1991

- Regulations on accommodation and alimentation of workers and the transport of workers from home to work and back; Official Gazette SFRJ No. 41/1968

- Regulations on equipment and procedures of first aid assistance and rescue team organization in case of work accidents; Official Gazette SFRJ No. 21/1971

- Regulations on general measures of protection at work from electricity on working facilities, working rooms and construction sites; Official Gazette SRS No. 21/1989

- Regulations on procedure for inspection and testing of working environment, dangerous materials, Working tools, installation and means and equipment for personal protection Official Gazette RS No. 7/1999

- Regulations on site arrangement project report cintents Official Gazette RS No. 31/1992

- Regulations on contents and issuing procedure for report on accident on work Official Gazette RS No. 2/1992

- Regulations on mens for personal protection on works and personal protection equipment Official Gazette RS No. 35/1969

- Legal act on minimum warranty period for some types construction structures and works Official Gazette RS No. /1997

B.	LIST OF STANDARDS AND TEHNICAL REGULATIONS

PBAB 87 	Regulation for concrete and reinforced concrete, 1987(PBAB 87) PPB 71.

JUS B.B2.010/1986 	Aggregate for concrete-Technical requirements

JUS ENV 197-1/1997 	Cement-Composition specifications and 					            conformity criteria Part 1: Common cements

JUS B.C1.014/1982 	Sulphate resisting cement-Portland cement, Portland blast furnace cement- Definition, classification and quality requirements

JUS U.M1.014/1959

JUS U.M1.015/1998 	Concrete-Concrete, hardened Determination of the depth of penetration of water under pressure

JUS U.M1.016/1992	Concrete-Method of test for resistance of concrete against freezing and thawing

JUS ISO 4848/1999	Concrete-Determination of air content on freshly mixed concrete-pressure method

JUS U.M1.034/1996 	Concrete-Admixtures for concrete. Definitions and classification

JUS U.M1.035/1996 	Concrete-Admixtures for concrete. Quality requirements and testing

JUS U.M1.037/1981 	Concrete-Admixtures for concrete previous testing

JUS ISO 4012/2000 	Concrete-Determination of compressive strength of test specimens

JUS U.M1.045/1982 	Transport and delivery of ready-mixed concrete

JUS U.M1.049/1998	Concrete-Coarse and hardened concrete-Taking, examination and testing in compression

JUS U.M1.050/1987 	Concrete-Concrete plant production suitability control

JUS U.M1.051/1987 	Concrete-Production control in the concrete plants

JUS U.M1.052/1987 	Concrete-Equipment for laboratories in concrete plants

JUS U.M1.055/1984	Concrete-Method of test for resistance of concrete against freezing

JUS U.M1.057/1984	Concrete-Grading of aggregate for concrete

JUS U.M1.058/1985	Concrete-Water for making concrete-Technical requirements and testing method

JUS ISO 1920/1997

JUS ISO 2736-1/1997	Concrete tests-Test specimens-Part 1: Sampling of fresh concrete

JUS ISO 2736-2/1997	Concrete tests-Test specimens-Part 2: Making and curing of test specimens for strength test

JUS B.B8.015/1984	Wear test-Grinding wheel method

JUS U.E3.050/1981	Prefabricated concrete units-Technical requirements for manufacture and mounting

JUS U.C9.400/1984

JUS-4 UB1.016

JUS.UB1.046

JUS.C-B4-.O81

JUS C-E4-020

JUS.C.D4-500

JUS.C.D4.020.

### APPENDIX 2: List of International Standards

  - List of applicable British Standards:

BS4:	Structural steel sections

BS405:	Specification for uncoated expanded metal carbon steel sheets for general purposes.

BS449:	Specification for the use of structural steel in building

BS497:	Specification for manhole covers, road gully gratings and frames for drainage purposes.

BS534:	Specification for steel pipes, joints and specials for water and sewerage.

BS639:	Specification for covered carbon and carbon manganese steel electrodes for manual metal arc welding.

BS 681:	Elastomeric seals.  Materials requirements for pipe joint seals used in water and drainage applications.

BS729:	Specification for hot dip galvanized coatings on iron and steel articles

BS743:	Specification for materials for damp-proof courses

BS812:	Testing aggregates.

BS882:	Specification for aggregates from natural sources for concrete

BS970:	Specification for wrought steels for mechanical and allied engineering purposes

BS1092:	Flanges and their joints – circular flanges for pipes, valves, fittings and accessories.

BS1186:	Timber for and workmanship in joinery

BS1200:	Specifications for building sands from natural sources

BS1243:	Specification for metal ties for cavity wall construction

BS1247:	Manhole steps

BS1305:	Specification for batch type concrete mixers

BS1369:	Steel lathing for internal plastering and external rendering

BS1370:	Specification for low heat Portland cement

BS1377:	Methods of test for soils for civil engineering purposes

BS1387:	Specification for screwed and socketed steel tubes and tubular and for plain end steel tubes suitable for welding or for screwing to BS21 pipe threads.

BS1470:	Specification for wrought aluminium and aluminium alloys for general engineering purposes: plate, sheet and strip

BS1474:	Specification for wrought aluminium and aluminium alloys for general engineering purposes: bars, extruded round tubes and sections

BS1485:	Specification for zinc coated hexagonal steel sire netting

BS1452:	Specification for flake graphite cast iron

BS1521:	Specification for waterproof building papers

BS1615:	Method for specifying anodic oxidation coatings on aluminium and its alloys

BS1706:	Method for specifying electroplated coatings of zinc and cadmium on iron and steel

BS1881:	Testing concrete

BS2789:	Specification for spherical graphite or nodular graphite cast iron

BS2853:	Specification for the design and testing of steel overhead runway beams.

BS2989:	Specification for continuously hot-dip zinc coated and iron zinc alloy coated steel of structural qualities: wide strip, sheet/plate and slit wide strip

BS3148:	Methods of tests for water for making concrete

BS3284:	Specification for polyethylene pipe for cold water services

BS3416:	Specification for bitumen-based coatings for cold application, suitable for use in contact with potable water

BS3505:	Specification for unplastiticized polyvinyl chloride (uPVC) pressure pipes for cold potable water

BS3506:	Specification for unplasticized PVC pipe for industrial uses

BS3600:	Specification for dimensions and masses per unit length of welded and seamless steel pipes and tubes for pressure purposes

BS3601:	Specification for carbon steel pipes and tubes with specified room temperature properties for pressure purposes

BS3692:	Specification for ISO metric precision hexagon bolts, screws and nuts. Metric units.

BS3921:	Specification for clay bricks

BS3987:	Specification for anodic oxidation coatings on wrought aluminium for external architectural applications

BS4027:	Specification for sulphate resisting Portland cement

BS4147:	Specification for bitumen-based hot-applied coating materials for protecting iron and steel, including suitable primers where required

BS4190:	Specification for ISO metric black hexagon bolts, screws and nuts

BS4315:	Methods of test for resistance to air and water penetration

BS4320:	Specification for metal washers for general engineering purposes.  Metric series

BS4346:	Joints and fittings for use with unplasticized PVC pressure pipes

BS4360:	Specification for weldable structural steels

BS4395:	Specification for high strength friction grip bolts and associated nuts and washers for structural engineering

BS4449:	Specification for carbon steel bolts for the reinforcements of concrete

BS4504:	Circular flanges for pipes, valves and fittings (PN designated)

BS4660:	Unplasticized polyvinyl chloride (uPVC) pipes and plastics fittings of nominal sizes 110 and 160 for below ground gravity drainage and sewerage.

BS4848:	Hot-rolled structural steel sections

BS4865:	Dimensions of gaskets for pipe flanges to BS 4504

BS4870:	Specification for approval testing of welding procedures

BS4871:	Specification for approval testing of welders working to approved welding procedures

BS4872:	Specification for approval testing of welders when welding procedure approval is not required

BS4887:	Mortar admixtures

BS4951:	Specification for builders' hardware: lock and latch furniture (doors)

BS5075:	Concrete admixtures

BS5135:	Specification for arc welding of carbon and carbon manganese steels

BS5155:	Specification for butterfly valves

BS5163:	Specification for predominantly key-operated cast iron gate valves for waterwork purposes

BS5215:	Specification for one part gun grade polysulphide-based sealants

BS5228:	Noise control on construction and open sites

BS5262:	Code of practice for external renderings

BS5328:	Concrete

BS5400:	Steel, concrete and composite bridges

BS5493:	Protective coating of iron and steel structures against corrosion.

BS5500:	Specification for unfired fusion welded pressure vessels

BS5606:	Guide to accuracy in building.

BS5628:	Use of masonry.

BS5642:	Sills and copings

BS5930:	Code of practice for site investigations

BS5950:	Structural use of steelwork in building.

BS6031:	Code of practice for earthworks

BS6073:	Pre-cast concrete masonry units

BS6089:	Guide to assessment of concrete strength in existing structures

BS6323:	Specification for seamless and welded steel tubes for automobile, mechanical and general engineering purposes

BS6399:	Loading for buildings.

BS7263:	Pre-cast concrete flags, kerbs, channels, edgings and quadrants

BS7352:	Specification for strength and durability performance of metal hinges for side hanging applications and dimensional requirements for template drilled hinges

BS8000:	Workmanship on building sites

BS8004:	Code of practice for foundations

BS8007:	Code of practice for design of concrete structures for retaining aqueous liquids

BS8110:	Structural use of concrete

B. List of applicable German Standards:

DIN488:	Reinforcing steel

DIN1045:	Structural use of concrete

DIN1048:	Testing methods for concrete

DIN1055:	Design loads for buildings

DIN1626:	Welded circular unalloyed steel tubes subject to special requirements, technical delivery conditions

DIN1910:	Welding

DIN1986:	Site drainage systems

DIN4021:	Soil; exploration by excavation and borings

DIN4034:	Prefabricated concrete and reinforced concrete manholes and inspection chambers

DIN4095:	Planning, design and installation of drainage systems protecting structures against water in the ground

DIN4099:	Welding of reinforcing steel

DIN4226:	Aggregates for concrete

DIN4235:	Compacting of concrete by vibrating

DIN18126:Subsoil: Testing procedures and testing equipment, density of non-cohesive soil, maximum and minimum density

DIN18196:Earthwork - soil classification for civil engineering purposes and methods for identification of soil groups

DIN18201:Tolerances in building: Terminology, principles, application, verification

DIN18203:Tolerances in building; precast concrete, reinforced concrete and pre-stressed concrete components

DIN50049:Documents on material tests: suggestions for the configuration of documents

DIN52123:Testing of bitumen and polymer bitumen sheeting and felts

DIN52143:Bitumen roofing felt with glass fleece base

C.	List of applicable ISO Standards:

ISO 1106:	Recommended practice for radiographic examination of welded joints

ISO 3452:	Non-destructive testing-penetrate inspection - general principles

ISO 4179:	Ductile iron pipes for pressure and non-pressure pipelines- centrifugal cement mortar lining - general requirements

D.	List of applicable ASTM Standards:

ASTM C 88:	Standard test method for soundness of aggregates by use of sodium sulphate or magnesium sulphate

ASTM C 150:	Standard specification for Portland cement

ASTM C 267:	Standard test method for chemical resistant mortars

ASTM C 307:	Standard test method for working and setting times of chemical resistant resin mortars

ASTM C 308:	Standard test method for working and setting times for chemical resistant mortars

ASTM C 321:	Standard test method for bond strength of chemical resistant resin mortars

ASTM C 413:	Standard test method for absorption of chemical resistant mortars, grouts and monolithic surfacing

ASTM C 531:	Standard test method for shrinkage and coefficient of thermal expansion of chemical resistant mortars, grouts and monolithic surfacing

ASTM C 579:	Standard test method for compressive strength of chemical resistant mortars and monolithic surfacing

ASTM C 580:	Standard test method for flexural strength and modulus of elasticity of chemical-resistant mortars, grouts, and monolithic surfacing

ASTM C 618:	Fly ash and raw or calcined natural pozzolan for use as a mineral admixture in Portland cement concrete

ASTM C 883:	Standard test method for effective shrinkage of epoxy-resin systems used with concrete

ASTM C 884:	Standard test method for thermal compatibility between concrete and an epoxy resin overlay

ASTM D 412:	Standard test methods for vulcanized rubber and thermoplastic rubbers and thermoplastic elastomers

ASTM D 1557:	Standard test method for laboratory compaction

ASTM D 2240:	Standard test method for rubber property - durometer hardness

ASTM E 110:	Standard test method for indentation hardness of metallic materials by portable hardness testers.

B. MECHANICAL PART

- DESCRIPTION

1. 	General

Subject of these Technical Specifications is Regional Water Supply System ĆELIJE and mechanical equipment in the next control systems:

- Pressure and Flow Control System  ĆIĆEVAC - direction to R. ĆIĆEVAC

- Pressure and Flow Control System VARVARIN - direction to R. VARVARIN

- Pressure and Flow Control System STALAĆ - direction to R.TODOROVA KULA

1.1. Pressure and Flow Control System ĆIĆEVAC - direction to R. ĆIĆEVAC

Position of the Flow Control System CICEVAC (direction to R. CICEVAC) in Regional Water Supply System ĆELIJE is shown on the Fig. 1.

The next hydro-mechanical equipment is installed in the Flow Control System CICEVAC:

1. Gate Valves (Short Body) [Isolating Valve]	                       DN250 / PN10	 4 pcs.

2. Flange Adapters (Dismantling Joint)			            DN250 / PN10  6 pcs.

3. Strainers								DN250 / PN10	 2 pcs.

4. Piston-Type Axial Flow Control Valves (Needle Valves)		DN250 / PN10	 2 pcs.

5. Manometers (pressure gauge) 0-10 bar and push button piston

(or three way tap)							4 compl.

6. Flow meters (specified and described in electrical part)		DN250 / PN10	 2 pcs.

7. Drainage pump with hose	(Q=141 l/min, H=5m, P=0.5kW)	1 compl.

Pipe dimension:

- DN1	=	DN400

- DN	=	DN250

- DN2	=	DN400

Dimension (pipe diameter and pipe length), way of connection are shown on drawings:

- M0-1	Layout o1-o1

- M0-2	Sections p1-p1 and p2-p2

1.2. Pressure and Flow Control System VARVARIN - direction to R. VARVARIN

The next hydro-mechanical equipment is installed in the Flow Control System VARVARIN (Fig. “Pressure and Flow Control System VARVARIN”):

1. Gate Valves (Short Body) [Isolating Valve]			DN250 / PN10	 4 pcs.

2. Flange Adapters (Dismantling Joint)				DN250 / PN10	 6 pcs.

3. Strainers								DN250 / PN10	 2 pcs.

4. Piston-Type Axial Flow Control Valves (Needle Valves)		DN250 / PN10	 2 pcs.

5. Manometers (pressure gauge) 0-10 bar and push button piston

(or three way tap)							4 compl.

6. Flow meters (described and specified in electrical part)		DN250 / PN10	 2 pcs.

7. Drainage pump with hose	(Q=141 l/min, H=5m, P=0.5kW)	1 compl.

Pipe dimension:

- DN1	=	DN400

- DN	=	DN250

- DN2	=	DN400

Dimension (pipe diameter and pipe length), way of connection are shown on drawings:

- M0-3	Layout o1-o1

- M0-4	Sections p1-p1 and p2-p2

1.3. Pressure and Flow Control System STALAĆ - direction to R.TODOROVA KULA

The next hydro-mechanical equipment is installed in the Flow Control System STALAĆ (Fig. “Pressure and Flow Control System STALAĆ”):

1. Gate Valves (Short Body) [Isolating Valve]		DN150 / PN10	 4 pcs.

2. Flange Adapters (Dismantling Joint)			DN150 / PN10	 6 pcs.

3. Strainer							DN150 / PN10	 2 pcs.

4. Piston-Type Axial Flow Control Valves (Needle Valves)	DN150 / PN10	 2 pcs.

5. Manometers (pressure gauge) 0-10 bar and push button piston

(or three way tap) 						4 compl.

6. Flow meter (specified in electrical part)			DN150 / PN10	 2 pcs.

7. Drainage pump with hose	(Q=141 l/min, H=5m, P=0.5kW)	        1 compl.

Pipe dimension:

- DN1	=	DN200

- DN	=	DN150

- DN2	=	DN200

Dimension (pipe diameter and pipe length), way of connection are shown on drawings:

- M0-5	Layout o1-o1

- M0-6	Sections p1-p1 and p2-p2

2. 	Technical Specification

Each of before mentioned Pressure and Flow Control Systems are equipped with next equipment:

- Piston-Type Axial Flow Control Valves (Needle Valves)

- Gate Valves (Short Body)

- Flange Adapters (Dismantling Joint)

- Strainers

- Manometers (pressure gauge) 0-10 bar  and push button piston (or three way tap)

- Drainage pumps

- Pipes and Fittings

- Supports

In these Technical Specifications are given description of before mentioned mechanical equipment.

2.1. Piston-Type Axial Flow Control Valves (Needle Valves, Plunger Valves)

| Description | Pressure and Flow Control System |  |  |
| --- | --- | --- | --- |
|  | CICEVAC | VARVARIN | STALAC |
| Size: | DN250 | DN250 | DN150 |
| Pressure rating: | PN10 | PN10 | PN10 |
| Test pressure: | 15bar | 15bar | 15bar |
| Fluid: | Water, clean (drinking water) | Water, clean (drinking water) | Water, clean (drinking water) |
| Connections | Flanges to DIN/ISO/EN standards | Flanges to DIN/ISO/EN standards | Flanges to DIN/ISO/EN standards |
| Operating gears and actuators | Manual and electric (max 2.2 kW) | Manual and electric (max 2.2 kW) | Manual and electric (max 2.2 kW) |
| Closing-opening time | linear closing and opening in min 210sec | linear closing and opening in min 210sec | linear closing and opening in min 180sec |
| Protection | IP68 | IP68 | IP68 |
| Materials: | Body: Ductile cast iron GGG-50 (EN-JS 1050) or GGG-40 (EN-JS 1030) Seal: NBR, EPDM, VITON, PUR Bearings: Brass, stainless steel/PTFE Corrosion protection: inside and outside EKB epoxy coating | Body: Ductile cast iron GGG-50 (EN-JS 1050) or GGG-40 (EN-JS 1030) Seal: NBR, EPDM, VITON, PUR Bearings: Brass, stainless steel/PTFE Corrosion protection: inside and outside EKB epoxy coating | Body: Ductile cast iron GGG-50 (EN-JS 1050) or GGG-40 (EN-JS 1030) Seal: NBR, EPDM, VITON, PUR Bearings: Brass, stainless steel/PTFE Corrosion protection: inside and outside EKB epoxy coating |
| Function: | As Regulating Valve Regulating Valves are used as pressure (upstream or downstream), flow and level regulating device. | As Regulating Valve Regulating Valves are used as pressure (upstream or downstream), flow and level regulating device. | As Regulating Valve Regulating Valves are used as pressure (upstream or downstream), flow and level regulating device. |

2.2. Gate Valves (Short Body)

| Description | Pressure and Flow Control System |  |  |
| --- | --- | --- | --- |
|  | CICEVAC | VARVARIN | STALAC |
| Fluid: | Water, clean (drinking water) | Water, clean (drinking water) | Water, clean (drinking water) |
| Size: | DN250 | DN250 | DN150 |
| Pressure rating: | PN10 | PN10 | PN10 |
| Test pressure: | 15bar | 15bar | 15bar |
| Function: | Gate Valves are resilient -seated isolating gate valves for “ON-OFF" service. The valve is closed by turning the hand-wheel in clockwise direction. | Gate Valves are resilient -seated isolating gate valves for “ON-OFF" service. The valve is closed by turning the hand-wheel in clockwise direction. | Gate Valves are resilient -seated isolating gate valves for “ON-OFF" service. The valve is closed by turning the hand-wheel in clockwise direction. |
| Max velocity | When using with technically pure liquids, as e.g. drinking water, flow velocities of up to 4m/s are admissible in fully open position. | When using with technically pure liquids, as e.g. drinking water, flow velocities of up to 4m/s are admissible in fully open position. | When using with technically pure liquids, as e.g. drinking water, flow velocities of up to 4m/s are admissible in fully open position. |
| Maintenance | Gate Valves are maintenance-free. The valve should be checked regularly for operative ness and tightness at a maximum interval of 4 years according to DVGW reference sheet W392. | Gate Valves are maintenance-free. The valve should be checked regularly for operative ness and tightness at a maximum interval of 4 years according to DVGW reference sheet W392. | Gate Valves are maintenance-free. The valve should be checked regularly for operative ness and tightness at a maximum interval of 4 years according to DVGW reference sheet W392. |
| Connections | Flanges to DIN/ISO/EN standards | Flanges to DIN/ISO/EN standards | Flanges to DIN/ISO/EN standards |
| Materials: | Body: Ductile cast iron GGG-50 (EN-JS 1050) or GGG-40 (EN-JS 1030) Stem Seal: Elastomer Stem: Ferritic chrome steel Corrosion protection: of body components: EKB epoxy coating, color “blue“, RAL 5015 | Body: Ductile cast iron GGG-50 (EN-JS 1050) or GGG-40 (EN-JS 1030) Stem Seal: Elastomer Stem: Ferritic chrome steel Corrosion protection: of body components: EKB epoxy coating, color “blue“, RAL 5015 | Body: Ductile cast iron GGG-50 (EN-JS 1050) or GGG-40 (EN-JS 1030) Stem Seal: Elastomer Stem: Ferritic chrome steel Corrosion protection: of body components: EKB epoxy coating, color “blue“, RAL 5015 |

2.3. Flange Adapters (Dismantling Joint)

| Description | Pressure and Flow Control System |  |  |
| --- | --- | --- | --- |
|  | CICEVAC | VARVARIN | STALAC |
| Fluid: | Water, clean (drinking water) | Water, clean (drinking water) | Water, clean (drinking water) |
| Sizes | DN250 | DN250 | DN150 |
| Pressure ratings | PN10 | PN10 | PN10 |
| Test pressure | 15bar | 15bar | 15bar |
| Application: | Dismantling joints are the units fitted within pipelines as connecting elements. They ensure easy and simple fitting of pipe fittings elements and measuring and control units by using the possibility of fitting length adjustments within +/- 1 limits. | Dismantling joints are the units fitted within pipelines as connecting elements. They ensure easy and simple fitting of pipe fittings elements and measuring and control units by using the possibility of fitting length adjustments within +/- 1 limits. | Dismantling joints are the units fitted within pipelines as connecting elements. They ensure easy and simple fitting of pipe fittings elements and measuring and control units by using the possibility of fitting length adjustments within +/- 1 limits. |
| Fabrication | Connecting dimensions of the flanges according to DIN / ISO / EN standards for PN10. The simple and reliable construction, effected by welding, satisfies all the requirements of safety and functional criteria. Sealing is accomplished by O-ring located in the groove formed by the housing and a sealing flange, which provides for subsequent tightening during the exploitation. | Connecting dimensions of the flanges according to DIN / ISO / EN standards for PN10. The simple and reliable construction, effected by welding, satisfies all the requirements of safety and functional criteria. Sealing is accomplished by O-ring located in the groove formed by the housing and a sealing flange, which provides for subsequent tightening during the exploitation. | Connecting dimensions of the flanges according to DIN / ISO / EN standards for PN10. The simple and reliable construction, effected by welding, satisfies all the requirements of safety and functional criteria. Sealing is accomplished by O-ring located in the groove formed by the housing and a sealing flange, which provides for subsequent tightening during the exploitation. |
| Material | The expansion joints parts fabrication is of structural steels. The sealing ring is produced of EPDM. | The expansion joints parts fabrication is of structural steels. The sealing ring is produced of EPDM. | The expansion joints parts fabrication is of structural steels. The sealing ring is produced of EPDM. |
| Maintenance | Maintenance-free. | Maintenance-free. | Maintenance-free. |

2.4. Strainer

| Description | Pressure and Flow Control System |  |  |
| --- | --- | --- | --- |
|  | CICEVAC | VARVARIN | STALAC |
| Fluid: | Water, clean (drinking water) | Water, clean (drinking water) | Water, clean (drinking water) |
| Sizes | DN250 | DN250 | DN150 |
| Pressure ratings | PN10 | PN10 | PN10 |
| Test pressure | 15bar | 15bar | 15bar |
| Application: | The flat strainers are the units used to prevent passing of minor foreign bodies and various impurities through the pipeline. In order to increase the safety during operation, they are fitted before the regulating needle valve. | The flat strainers are the units used to prevent passing of minor foreign bodies and various impurities through the pipeline. In order to increase the safety during operation, they are fitted before the regulating needle valve. | The flat strainers are the units used to prevent passing of minor foreign bodies and various impurities through the pipeline. In order to increase the safety during operation, they are fitted before the regulating needle valve. |
| Fabrication | The flat strainers are fabricated for pressures PN10 with connecting dimensions of the flanges according to DIN / ISO / EN standards. The housing is made in one piece and the pipeline is connected by means of flanges. The filter comprises a sieve, of corresponding density - regulating valve requirements. Sieve replacing and cleaning is done in a simple way, by removing the cover and taking the sieve out. | The flat strainers are fabricated for pressures PN10 with connecting dimensions of the flanges according to DIN / ISO / EN standards. The housing is made in one piece and the pipeline is connected by means of flanges. The filter comprises a sieve, of corresponding density - regulating valve requirements. Sieve replacing and cleaning is done in a simple way, by removing the cover and taking the sieve out. | The flat strainers are fabricated for pressures PN10 with connecting dimensions of the flanges according to DIN / ISO / EN standards. The housing is made in one piece and the pipeline is connected by means of flanges. The filter comprises a sieve, of corresponding density - regulating valve requirements. Sieve replacing and cleaning is done in a simple way, by removing the cover and taking the sieve out. |
| Material | The impurities traps housing is made of structural steels by welding (or ductile cast iron), and the filter comprises a stainless steel sieve. | The impurities traps housing is made of structural steels by welding (or ductile cast iron), and the filter comprises a stainless steel sieve. | The impurities traps housing is made of structural steels by welding (or ductile cast iron), and the filter comprises a stainless steel sieve. |
| Maintenance | Maintenance-free. The frequency of cleaning depends on the operating fluid fouling degree. | Maintenance-free. The frequency of cleaning depends on the operating fluid fouling degree. | Maintenance-free. The frequency of cleaning depends on the operating fluid fouling degree. |

2.5. Manometers (pressure gauge) with push button piston (or three way tap)

Upstream and downstream of each regulating Needle Valve are placed manometer (pressure gauge) with push button piston (or three way tap).

Measurement range for manometer: 0-10bar

2.6. Drainage pump

| Description | Pressure and Flow Control System |  |  |
| --- | --- | --- | --- |
|  | CICEVAC | VARVARIN | STALAC |
| Fluid: | Drainage water with a maximum solids content of 0.5% | Drainage water with a maximum solids content of 0.5% | Drainage water with a maximum solids content of 0.5% |
| Capacity (l/min) | app 141 | app 141 | app 141 |
| Head (m) | app 5 | app 5 | app 5 |
| Power P1 (kW) | 0.5 | 0.5 | 0.5 |
| Application: | Submersible pump for clear and surface water (with a maximum solids content of 0.5%). With hose and ready to plug-in, with built-in level control and with built-in check-valve (Discharge outlet G 1 1/ 4). The check-valve built into the discharge blocks prevents return-flow from the discharge line when the pump is switched off. The pump and motor section form a pressure-tight encapsulated unit, with motor housing constructed from corrosion resistant material. | Submersible pump for clear and surface water (with a maximum solids content of 0.5%). With hose and ready to plug-in, with built-in level control and with built-in check-valve (Discharge outlet G 1 1/ 4). The check-valve built into the discharge blocks prevents return-flow from the discharge line when the pump is switched off. The pump and motor section form a pressure-tight encapsulated unit, with motor housing constructed from corrosion resistant material. | Submersible pump for clear and surface water (with a maximum solids content of 0.5%). With hose and ready to plug-in, with built-in level control and with built-in check-valve (Discharge outlet G 1 1/ 4). The check-valve built into the discharge blocks prevents return-flow from the discharge line when the pump is switched off. The pump and motor section form a pressure-tight encapsulated unit, with motor housing constructed from corrosion resistant material. |
| Construction | Connection chamber with cover and watertight cable inlet and strain relief. Outer jacket and other housing parts made of corrosion resistant synthetic material. Motor is dynamically balanced with temperature monitor in the stator, which switches off the pump in the case of overload. Shaft is made of stainless steel. The sealing on the motor side is by means of special lip seals supported by lubricated bearings. The medium being pumped flows around the motor housing for optimum heat dissipation. The pump unit has a built in automatic level control, with easily removable float cover for cleaning purposes. The special bayonet clamping allows the screen to be removed by hand in the event of an impeller inspection. | Connection chamber with cover and watertight cable inlet and strain relief. Outer jacket and other housing parts made of corrosion resistant synthetic material. Motor is dynamically balanced with temperature monitor in the stator, which switches off the pump in the case of overload. Shaft is made of stainless steel. The sealing on the motor side is by means of special lip seals supported by lubricated bearings. The medium being pumped flows around the motor housing for optimum heat dissipation. The pump unit has a built in automatic level control, with easily removable float cover for cleaning purposes. The special bayonet clamping allows the screen to be removed by hand in the event of an impeller inspection. | Connection chamber with cover and watertight cable inlet and strain relief. Outer jacket and other housing parts made of corrosion resistant synthetic material. Motor is dynamically balanced with temperature monitor in the stator, which switches off the pump in the case of overload. Shaft is made of stainless steel. The sealing on the motor side is by means of special lip seals supported by lubricated bearings. The medium being pumped flows around the motor housing for optimum heat dissipation. The pump unit has a built in automatic level control, with easily removable float cover for cleaning purposes. The special bayonet clamping allows the screen to be removed by hand in the event of an impeller inspection. |

2.7. Pipes and fittings

All pipes, fittings and flanges are of structural steel. Corrosion protection corresponds to the working conditions and the chemical-mechanical characteristics of the working medium.

| Dimensions of welded steel tubing and pipes |  |  |  |
| --- | --- | --- | --- |
| Nominal diameter | Outside diameter (mm) | Thickness (mm) | Weight (kg/m) |
| DN100 | 108 | 2.9 | 7.57 |
| DN125 | 127 | 3.2 | 9.84 |
| DN150 | 159 | 4.0 | 15.4 |
| DN200 | 219.1 | 4.5 | 23.7 |
| DN250 | 273 | 5.0 | 33.0 |
| DN300 | 323.9 | 5.6 | 43.8 |
| DN350 | 355.6 | 5.6 | 48.2 |
| DN400 | 419 | 6.3 | 64.3 |

All connection of fittings and valves in pumping stations are with flanges. The flanges installation (connecting) dimensions correspond to standards ISO EN for nominal diameter DN and nominal pressure PN10.

Flanges connect with bolts. The number and size of bolts conforms to the same standard as for the flanges (nominal pressure PN10).

2.8. Supports

All supports are of structural steel. Corrosion protection corresponds to the working conditions and the chemical-mechanical characteristics of the working medium.

- GENERAL CONDITIONS

1. General Provisions

1.1. Submittals

The Contractor shall submit all his submittals to the Engineer in writing at least 30 days before commencing the relevant item of work.

1.2. Staff

The Contractor shall submit to the Engineer the list of operatives that he intends to employ to execute successfully the works of the erection and installation of mechanical equipment. This list of the personnel shall be arranged according to each specific application of installation and shall contain the full names, years of experience in that particular specialty and, if and where required, the certificates showing the operatives particular ability.

1.3. Means of Transportation (Haulage)

The Contractor shall provide all necessary means for moving the equipment on the site. The Contractor shall submit to the Engineer the list of types and methods of internal transportation that shall be used during performing the works on and around the site. That shall include the means for loading on and unloading the equipment out of vehicles, means for storage of the equipment, means for hauling equipment from the storage to the location of installation, temporary lifting devices and appurtenances for positioning the equipment at the place of installation.

The list of transportation means shall include their basic technical characteristics, such as the carrying and/or lifting capacity and the weight of unloaded vehicles.

The Contractor shall use his lifting devices

All means of transportation used by the Contractor shall be serviceable and certified accordingly, as required by relevant Serbian Standards.

The haulage is the necessary haulage within the site for the movement of the equipment, the piping, etc. from the Contractor’s store to the installation point.  The haulage includes loading, unloading, etc.  The haulage works are included in the Contractor’s prices for installation and no additional increment shall be paid for it.

The ways of haulage and the means of haulage shall be coordinated in advance with the Employer and the Engineer in order to prevent damage to existing facilities and disturbance or harm to the work of other Contractors at the site.

The haulage shall be undertaken by the Contractor in a way that shall avoid all harm to the equipment being hauled, the penetration of dirt into it, etc.

The haulage shall be undertaken with professional equipment by professional, skilled and licensed manpower.

1.4. Machines, Tools and Instruments

At least 30 days before installing the Equipment the Contractor shall submit to the Engineer the list of machines, tools and instruments necessary to perform the specified works. The list shall schedule but not limited to the names, brands and basic technical characteristics of the following:

- portable diesel generator

- tools for cutting the steel plates and pipes and preparing the edges of pipes for welding

- welding machines and accessories according to welding technology for pipes

- welding testing machines and instruments

- machines and accessories for brazing

- tools for male and female threading of pipes

- micrometers

- feeler, strip and dial gauges

- square and parallelism checking instruments and tools

- calibrated spirit levels

- drilling equipment

- wrenches and non-adjustable spanners with  dial indicator

- torque wrenches

- certified slings, straps and chain hoists

- V-belt tension tools

- vibration meters

- all other tools and instruments necessary for proper installation of the equipment

- sand blasting machines, tools for applying anti-corrosion protection and instruments to test the quality of anti-corrosion coatings

- Equipment and instruments necessary for hydrostatic and leakage testing of pipelines during and after completion of the works, such as portable high pressure air compressor, plunger pump, gauges, etc.

Tools and instruments intended to be used shall be designed for the precise application and measurement. It is obligatory that the scale on all the Instruments shall be in the SI system of measurement.

Abnormal wear and tear of parts of equipment through the use of improper tools during assembly is not acceptable. At take-over, equipment shall be in ''as-new'' condition.

In the early stage during construction, a check should be made on the availability of special tools that shall be supplied by the Supplier/Employer. Such special tools as provided may be used by the Contractor as and when required, if approved by the Engineer. In such cases, the Contractor shall remain responsible for hand-over of these tools to the Employer in ''as-new'' condition. Throughout the implementation of the Works, preservation of special tools should be maintained.

1.5. Materials

The Contractor must indicate the names of manufacturers of all consumption materials, such as lubricants, coatings, etc., as well as fixing and levelling elements which are not delivered by the manufacturers (electrodes, spindles, jack screws, shims and similar), along with the relevant characteristics of these materials. These shall be to the approval of the Engineer.

1.6. Documentation to be prepared by the Contractor

The Contractor shall prepare the following technical documentation:

- plan for implementation of the mechanical works that shall define the Contractor's organization structure, quality assurance and quality control plan, sequence of activities and timing set out

- plan of equipment transportation that mainly shall concern of means and methods of internal transportation inside the structures, including auxiliary lifting devices and arrangement of temporary or permanent lifting hooks and/or anchorages

- erection and installation plan that shall concern of activities sequence for each particular facility, details of positioning, levelling and axes cantering  of the equipment during erection, and fixing equipment to the adjacent during installation, including  auxiliary supports and auxiliary lifting devices

- welding plan that shall concern of welding methods and materials, welding procedures and  welding acceptance/testing plan

- plan of pipelines cleaning and disinfection (that might be a part of the general plan for cleaning and disinfection of Water Treatment Plant)

- plan of pipelines hydrostatic and leakage test that shall mainly concern sequences in sectional testing, including technology of preparation the pipelines section for testing,  filling  the pipelines with testing fluid, empting, re-filling and repeating the testing  where necessary

- shop drawings of equipment that shall be manufactured on the site such as pipe fittings (elbows and branches) and pipes steel supports and hangers, including embedded parts ( anchorages)

- plan for testing during and after completion of  the works

- all records concerning inspection and testing during and after completion of the works

- test reports

- progress reports and dairy of daily activities

The documents that shall be prepared 42 days after the Commencement date and shall be developed on the basis of the plans, methodologies and procedures as they are defined in this Technical Specification and/or elaborated in separate documents. During the implementation of the Contract, the Engineer shall remit the Contractor with full details of the project including drawings and other documents, as well as the installation instruction of the manufacturers. The Contractor’s documents should be in accordance with commonly recognized engineering practices. The required documents must be submitted to the Engineer for his approval.

1.7. Alternation and Deviation

The works to be done shall be performed strictly in accordance with the requirements of this Technical Specification and Drawings, including all alternations that are mutually agreed upon between the Contractor and the Employer during the period of negotiation.

During construction period, any change, alternation, modification or deviation to the drawings and specified requirements must be notified in advance to the Engineer to his prior approval. Without Engineer’s prior authorization, the Contractor mast not commence of works that might deviate from the requirements defined in the Specification.

1.8. Conformity to Standards

The works to be done, where this is applicable, shall conform to the recognized international and/or domestic standards. The specification, in general, refers to the following standards:

AWWA		American Water Works Association

BS		British Standards Institution

CEN		European Committee for Standardization

CP		British Standards Institution (Code of Practice)

DIN		German Industrial Standards

EN		Euro-norm - European Community Standard

IEE		Institution of Electrical Engineers

IEC		International Electro-technical Commission

ISO		International Organization for Standardization

SI		International System of Units

SIS		Swedish Standards Commission

WIS		British Water Industry Standard

JUS		Yugoslav Standards and Regulations (current Serbian standards)

If particular points are indicated, in which the Specification does not conform to those standards, the requirements of the Specification shall prevail.  The order of prevalence shall be as follows:

Technical specifications (General or Specific)

Quoted Standard: JUS Standard or any other Standard which the Contractor suggests and the Engineer agrees upon.

1.9. Implementation and Control of Works

The Contractor shall provide all staff, equipment, devices, tools, consumable materials, instruments and documentation necessary for erection, installation, testing and commissioning of the equipment specified in the Technical Specification.

The Contractor shall implement the specified works in accordance with the requirements of the Technical Specification, contractual provisions, statutory procedures and legal requirements (policy) of Serbian Government.  The Contractor shall be fully responsible for the organization of the site, implementation and quality of the works, and shall bear all constraints relating to any lack of organization and coordination of activities, location and operation of his equipment and shall be unable to claim compensation for any reason whatsoever except in fully justified circumstances beyond his control.

The Contractor shall commence with the setting out of the equipment after receiving the Engineer's approval on the relevant documents.

The Contractor shall have in effect at all time a quality assurance and quality control plan which clearly establish the authority and responsibility of those responsible for quality assurance and quality control of the works. Persons authorized to perform quality functions shall have sufficient and well defined responsibility and authority to enforce quality requirements, to identify quality problems, initiate, recommend and provide solutions and verify the effectiveness of solutions.

The Contractor and each of his subcontractors shall submit the QA and QC plan and nominate the quality assurance personnel whose solo duty is quality assurance and quality control and who carries a defined quality assurance and quality control position within the Contractor’s organization plan. All as described in GTS, Chapter 2, Item 2.6.

The Contractor shall be fully responsible for his subcontractors. He shall identify and forward to his subcontractor all applicable quality assurance and quality control requirements imposed by the Specification and shall ensure compliance thereto. The QA and QC plan of each subcontractor shall be approved by that subcontractor’s management and in its entirety shall be approved by the Contractor’s management. QA and QC plans of the Contractor and his subcontractors shall be submitted to the Engineer to be reviewed for compliance.

The quality control program applicable to site activities shall address the following as a minimum:

•	Internal transportation

•	Material and equipment identification

•	Erection and installation

•	Welding and associated processes

•	Calibration of measuring and testing equipment

•	Inspections and testing

•	Control of non-conformances

•	Documentation control

•	Records control

The Engineer may periodically monitor the Contractor’s (and/or his subcontractor’s) conduct of works to assure compliance with Contract Documents.

The Engineer shall be given access to the works at all reasonable times. All specific quality documentation such as staff qualification, inspection and testing plans and/or records related to the works shall be readily available upon request. Materials, equipment and services shall be subjected to all inspections and tests required by applicable codes and standards in addition to those explicitly called for in the Specification and/or defined in the Contractor’s plan for testing during and after completion of the works.

Any deficiency noted during Engineer’s review of the works may cause holding on the works. The responsibility of the Contractor for organization, performing, quality and timing of the works shall not prevent the Engineer, in the event of incorrect procedures that might damage the equipment, bring into danger the quality of works and/or slow-down the progress of the works, from proceeding to issue instructions and take precautionary measures to make up for these lacking, at the expense of the Contractor who shall be advised immediately.

Review performed by the Engineer shall not relieve the Contractor (or his subcontractors) of his obligation to perform the works according to requirements of the Specification and approved documentation of his own, and to keep the works in progress as it is defined in the Contract Document.

In his erection and installation plan the Contractor shall establish mandatory hold points relating to erection and installation activities that progress in sequential phases. Mandatory hold points are considered to be those requiring reconnaissance of the Engineer and beyond which, the Contractor shall not proceed to the sequential phase without written consent of the Engineer. Hold points require receipt of notification at least one working day in advance of the scheduled time of performance. The Engineer may require that activities performed without proper notification are repeated for engineering observation at the Contractor’s expense. The Engineer may witness the event or authorize the Contractor to proceed without the Engineer witnessing the event.

The waiver of any inspection and test and/or witnessing thereof by the Engineer shall not relieve the Contractor of his responsibility to meet fully the requirements of the Specification.

The following are the hold points for which the prior notification is required:

•	Levelling, alignment, clearance checking and fixing of the equipment

•	Applying of anti-corrosion protection

•	Welding

•	Hydrostatic pressure tests

•	Hydro/pneumatic leakage tests

•	Functional tests

•	Operational tests

•	Non-destructive tests

•	Major repairs

1.10. Erection and Installation

Erection and installation requirements that are specified for different types of equipment should be understood in a broader sense that suppose all activities as it is scheduled in the Scope of Works.

Erection and installation of the equipment shall be done strictly in accordance with manufacturer's installation and operation procedures and requirements specified hereinafter. The requirements specified hereinafter are not presented to replace activities that shall be specifically recommended by manufacturers and submitted to the Contractor in the form of I & O Manual.  Special requirements are presented here to supplement manufacturer's instructions, or to merely serve as reminders and guidance of activities that shall be taking place. As a rule, these requirements shall first defer to the manufacturer’s instructions on installations and putting equipment into operation. In the case when there are no specific manufacturer instructions for some portion of works that is required by this Specification, requirements of this Specification are mandatory.

After the completion of the installation, the checks and the grouting, the Contractor shall prepare the equipment or the piping for the stage of performing the functional tests by carrying out the following works:

- Dismantling and removal of all the ancillary means used for the installation, including temporary supports, ladders and temporary stages, the grout frames, etc.

- Cleaning the installation site of all refuse, paint remnants, cement remnants, grout, etc.

- Paint repairs: the last stage of the installation of equipment or piping is repairs to the paintwork.  The Contractor shall check carefully the paint on the equipment and shall make repairs, using the original paint which is to be provided by the Contractor.  The work is to be done through professional industrial painters and not by one of the members of the installation team.

- Protection of the steel screws and bolts by painting them, according to the directive of the Engineer.

1.11. Auditing, Inspection and Testing

This Clause shall specify some general provisions regarding auditing, inspection and testing of mechanical works.

The Engineer has the right to audit the Contractor and inspect and witness the works to ensure full compliance with the requirements of the Specification, drawings, codes, standards and approved submittals.

Auditing shall refer to progress of the works and shall mainly concern of the progress reports and the diary of daily activities.

Inspection shall refer to documentation control, visual examination of quality of the Works, identification and control of procedures, tools, materials and technologies applied before, during and after performing the Works, examination of measuring records relating to installation instruction (certificates of calibration for instruments used in quality control process, dryness of welding electrodes, tolerances of levelling, positioning and alignment of the equipment, torques applied during bolting of valves and fittings) and examination of records of various tests.

The Engineer during inspections shall not give any approval to the adequacy of the work in progress.  Deficiencies, defects and imperfections noted during any inspection may be a cause for rejection of the Work and the Contractor shall be liable to rectify the work at his own expense.

The Contractor shall at his own cost and expense perform the tests required in the Specification in accordance with provisions thereof and that of applicable standards. Before commencing the tests, whether test procedures specified or not in other documents, the Contractor shall submit to the Engineer for approval Test Method Statement with described methods and relevant standards by which he proposes to perform the tests.

All materials and labour for carrying out the tests specified in the Specification shall be provided by the Contractor.

The Contractor shall submit the certified test reports showing test conditions (an outline of the testing procedure, brief description of the methodology and standards applied, list of instruments, instrument certificates, testing duration, name and certification/qualification of test team leader) and test records to the Engineer for review and acceptance. When specified test have been successfully passed the Engineer shall issue a certificate to the Contractor, to that effect.

Testing shall refer to the quality of the Works. In cases that tests fail to meet the quality requirements of the Specification and/or approved codes and standards, the Contractor shall take remedial measures on their own expense to improve the Work and retest it to the satisfaction of the Engineer. Before implementation, the remedial plan shall be approved by the Engineer.

According to the progress of the Works the tests required to be performed are generally divided to the following:

•	Tests during the Works

•	Tests on completion the Works

•	Tests after completion of the Works

The tests during the Works are considered to be the tests that have to be performed at various stages of progress, or the tests that might be done partially on some portions of the Works.

If a section of Works is fully completed while the rest of the Works is in progress, this section of the Works may be fully tested with the permission of the Engineer.

The tests on completion of the Works may be classified in the following activities:

- Pre-commissioning tests

- Commissioning tests

- Trial run

Depending on type of the equipment the following tests during works and on completion shall be performed:

- testing of anti-corrosion protection

- non-destructive testing of all field welds

- pressure test of all pipelines

- hydro/pneumatic leakage tests

- functional test of all equipment installed

- operational test of all installation

If some of tests fails to meet the quality requirements regardless whether it is solely caused by imperfections in installation or equipment supplied or it is caused by both installation and equipment imperfections, the Contractor shall take on his own expense all necessary remedial measures to repair such defects, including dismantling of defective equipment, and if necessary transporting of such equipment to the workshop or the Supplier vehicle, loading the equipment on the Supplier vehicle and unloading when returned, transportation to the place of installation, reinstallation and repeating the tests to the satisfaction of the Engineer.

The pre-commissioning tests shall start with preliminary activities.

Preliminary activities shall mainly concern the preparations that shall enable the later ones to be performed successfully. These activities shall not relate only to the labour but to the organization of the later activities.

Preliminary activities shall include final inspection of installation works, final inspection of electrical works related to mechanical equipment, cleaning of pipelines and reservoirs, and filling up the pipelines and reservoirs with water or gas.

Functional tests shall be performed either during the Works or during the period of pre-commissioning activities (start-up activities).  Functional tests shall be performed, wherever applicable, on each piece of equipment, in dry (during the Works) or wet conditions (after completion of the Works). In general that means starting of equipment in a very short period of time to prove that equipment is functioning, that there are no obstructions that might cause any damage during start-up and that wiring of the equipment is correctly done.

After functional and pressure tests are successfully performed and test results accepted by the Engineer, the first start-up of installations shall be performed. During these activities, the installations shall be carefully observed, all faults such as excessive vibrations or noises from the equipment and pipelines, leakages, malfunctions of instruments and any other defects shall be notified and corrected to the satisfaction of the Engineer.

Hydro/pneumatic leakage tests shall be performed on all hydraulic and pneumatic installations in order to detect the leakages that might occur at equipment sealant or pipeline and valve joints and that might be the result of installation imperfections or damages caused during internal transportation, installation and improper handling. The leakages shall be observed during start-up activities and especially during operational tests. The tests shall satisfy the requirements of the Specification and approved codes and standards. In cases where tests fail to meet specified requirements the Contractor shall repair imperfections at his own expense and retest the installation to the satisfaction of the requirements of the Specification.

If it is evident that leakages are caused by errors in the manufacturing of Equipment, such malfunctions shall be referred to the Supplier and repaired at the manufacturers’ expense, but all works related to dismantling, internal transportation, reinstallation and retesting shall be at the expense of the Contractor.

After pre-commissioning tests are successfully conducted in accordance with the design requirements, the certified reports shall be submitted to the Engineer for his acceptance. After Engineers approval of the pre-commissioning tests, the Contractor shall commence the commissioning tests

Operational tests shall be performed during commissioning. During this period the Works and equipment shall be subjected to all operating conditions they are designed for, in order to provide evidence of safe operation and conformance to the Specification. During the operational tests, the Contractor shall record all specified measurements. Test reports shall contain the schedule of personnel who shall perform the tests, the title of installations, the date of test performance, description of operations, records of conditions under which the test is performed, records of measurements that are conducted during testing, duration of testing and comments based on observations made during testing. After the tests are successfully conducted in accordance with the design requirements, the certified reports shall be submitted to the Engineer for his acceptance. If an operational test of the particular installation fails to meet the specified requirements in any aspect, notified defects and/or malfunctions shall be corrected, and test shall be repeated at the Contractor’s expense and to the satisfaction of the Engineer. The Contractor expense shall include all works that are the consequence of repeating tests, except repairing works on the equipment that shall be performed by the Manufacturer at their expense.

All kinds of tests in all execution phases, functional, operating and performance testing shall be performed in the presence of the Supplier or his representatives who are responsible for their portion of the Works (equipment guarantees).

2. Manufacturing and Workmanship

2.1. General

All equipment shall conform to the applicable standards regarding material, workmanship, design, and tests. Tolerances, fits, and finishes shall conform with the best modern shop practices in manufacturing of finished products of a nature similar to those covered by the Specification. All equipment shall be of rugged durable construction, designed for frequent operation.

All work shall be performed and completed in a thorough workmanlike manner and shall follow the best modern practice in the manufacture of high-grade equipment, notwithstanding any omissions from the Specification.

Should any departure from a Contract drawing occur during manufacturing, the nature of the departure and the proposed method of rectification shall be reported in writing by the Contractor to the Engineer, and the Engineer may decide whether the item of plant concerned should be rectified, or is acceptable.

Acceptance of rectification methods by the Engineer shall in no way relieve the Contractor of his obligation to supply materials, which meet the requirements of the Contract.

2.2. The Works to be done in the Workshop

All cutting, chamfering and other shaping of metals necessary for the field connections shall be done in the Contractors workshop. Adequate temporary bolted field connections shall be provided to hold the assemblies rigidly and in proper alignment during shop and field assembly. To assure proper alignment during field erection, a minimum of 2 dowels shall be provided for each field connection between subassemblies. The holes shall be drilled and the dowels fitted at shop assembly after the subassemblies have been satisfactorily aligned. All stipulations for welding, structural work or other, shall be applied to field work as well as to shop work, except where otherwise stated.

2.3. Tolerances

Tolerances shall be defined on the drawings. Separate tolerances shall be defined, one set for manufacturing purposes and another set for installation purposes.

2.4. Temporary Bracing

Temporary bracing and attachments shall be removed exercising care that the base metal to which they are attached is not adversely affected. Projecting welds remaining after this operation shall be chipped and ground flush. Tears in the base metal shall be welded up and ground flush.

2.5. Machine Work

All surfaces that are indicated on the Drawings or those that require machining for their intended function, or those that are usually machined according to good workshop practice shall be machined.

The quality of the surface finish shall be adequate for the intended use and shall be in accordance with ANSI-B4.1 "Surface Texture". Compliance with the specified surface shall be determined by sense of feel and by visual inspection of the Work compared to standard roughness specimens, in accordance with the provisions of ANSI - B46.1.

Machine-finished surfaces shall be thoroughly cleaned of foreign matter. Finished surfaces of large parts and other delicate surfaces shall be protected with wooden pads or other suitable means. Unassembled pins and bolts shall be oiled and wrapped with moisture resistant paper or protected by other suitable means.

Finished surface of ferrous metals to be in bolted contact shall be washed with a rust inhibitor and given one thin coat of white or blue lead and proper oil.

So far as practicable, all work shall be laid out to secure proper matching of adjoining unfinished surfaces. Where there is a large discrepancy between adjoining unfinished surfaces they shall be chipped and ground smooth, or machined, to secure proper alignment. If surfaces not designated as finished but require machining to obtain the tolerances or straightness specified or needed for correct function, such machining shall be performed by the Contractor free of charge.

3. Metal Works

3.1. Embedded Metal Work

Unless otherwise specified, any foundations, wall and roof openings and coverings, concrete floor filling, sleeves in foundations and walls and trenches with floor plates for cables, will be provided by the Contractor. Civil works are detailed in a separate specification.

The Contractor shall supply, all anchors, fasteners, embedded metalwork, and sleeves associated with and required for the installation of the equipment, except if otherwise mentioned in the Specifications.

The Contractor will be responsible for the determination and details of all loads and forces exerted by the equipment that are transferred to the foundation.

The Contractor shall show the location and full details of all embedded components on his shop drawings and ''as made'' drawings and shall be responsible for the complete content and accuracy of his drawings and the information supplied to others. Anchorage's to be embedded in primary concrete will be installed by the Contractor according to the design i.e. approved foundation drawings.

All adjustments to foundation levels, bedding and grouting of equipment on foundations and cementing into walls and floors will be carried out by the Contractor.

The portion of any steelwork, which is to be built into the concrete foundations, shall not be painted or coated unless otherwise approved or specified.

3.2. Miscellaneous Metalwork

Except where otherwise indicated elsewhere in the Special Technical Requirements, the Contractor shall supply and install the following:

- All necessary floor-plates and curbing, including manhole covers, covers for pipe and cable trenches, required for completing the floors around and over plant supplied under the Contract.

- All platforms, ladders, guards and handrails necessary for easy and safe access to equipment supplied under the Contract.

- Safety guards at each point where normal access provision would permit personnel to come within reach of any moving equipment.

3.3. Floor Loads

All mechanical parts or equipment can only be temporarily stored or assembled on specially indicated areas in the Water Treatment Plant. The Contractor will provide a load indication drawing for the Engineer’s approval.

4. Welding

4.1. General

The field welding process shall be applied to jointing the sections of carbon steel  pipes, jointing flanges to steel pipes, jointing sections of stainless steel pipes, manufacturing of pipes steel supports, hangers and brackets and fixing them to anchor plates, welding  the cranes rail fixing elements to anchor plates, etc. In addition, the welding works shall include all preparation and/or finishing/repairing works on parts to be welded and non-destructive examinations of welds.

The welding shall be performed on the basis of the relevant drawings and/or approved Contractor’s drawings, and on the basis of the welding process, approved by the Engineer.

The Contractor shall furnish and well maintain all equipment necessary to permit welding operators to follow the welding procedures and obtain results prescribed. This includes welding machines and accessories, as well as equipment and materials for non-destructive examination of welds.

Welding shall be performed by manual shielded metal-arc welding process that shall produce a joint meeting the minimum strength requirements of the base metal and meet the requirements of welding procedure as per approved standard. The Contractor may propose other specific process or combination of processes when considering it necessary to meet the specified requirements.  Such proposals shall be subject to Engineer’s approval.

4.2. Welding Procedure

Based on the properties of base material, shape, size and position of equipment that have to be subjected to, or manufactured by welding, the Contractor shall submit to the Engineer for approval, the welding procedure which shall be based on the requirements specified hereinafter. In the welding procedure, the Contractor shall propose the type of welding process and welding standards he is intended to use. For each of the proposed methods of welding, the Contractor shall list the welding equipment and accessories to be used in the field (including equipment for non-destructive examination of welds), as well as equipment characteristics. In addition, the Contractor shall submit the list of qualified welders and inspectors with their certificates and evidence of their engagement in work on products involving the proposed welding procedure.

The welding procedure shall include the following:

• Welding process and standard applied:

Welding shall be performed by manual shielded metal-arc welding process that shall produce a joint meeting the minimum strength requirements of the base metal. The Contractor may propose other specific arc welding process or combination of processes. The welding process shall be in accordance with Serbian standards (JUS) or equal. Gas (oxy-acetylene) welding may exceptionally be allowed (for sections of steel pipes smaller than DN150).

• Equipment:

The Contractor shall designate the equipment to be used. That shall include the technical characteristics (electrical characteristics, flame/arc characteristics, composition of shielding gas and range of gas flow, type of shielding flux, characteristic of all instruments, etc.)

• Pipes and fittings:

All materials to which specific welding process is applied shall be identified.

• Diameter group-wall thickness group:

The diameters and wall thickness of the range of pipes and fittings, and range of crane rails and I beams over which the welding procedure is applicable shall be identified.

• Joint design:

The Contractor shall also submit to the Engineer a sketch showing the shape and dimensions of pipe to pipe, pipe to flange and pipe to fitting joints. This shall include the angle of bevel, size of root face, size of root opening or space between abutting members, and the shape and size of fillet welds. The type of backup ring or consumable insert ring shall be designated, if it is intended to be used. Arrangement of tack welds and method of their removal shall be designated, if used.

• Root run:

The Contractor shall propose the methods of making initial root run in butt joints.

• Filer metal and number of beads:

Types and sizes of filler metal, number and sequence of beads, and direction of welding shall be designated.

• Time lapse between passes and speed of travel:

Maximum time between the competition of root pass and start of next bead pass, time between the competition of one bead pass and start of other, and speed of travel for each pass shall be designated.

• Pre-heat and post-heat:

If pre-heat and post-heat treatment is to be applied, the methods, temperature, temperature control, ambient temperature, etc. shall be specified.

• Cleaning:

Power or hand cleaning tools shall be clearly listed.

• Inspection and testing:

The Contractor shall provide a full-time certified weld inspector who shall inspect the welding works and conduct the required testing. Methods of non-destructive testing shall be in accordance with applied welding standard. Equipment and instruments for non-destructive testing shall be listed.

All welds shall be performed strictly in accordance with approved welding procedure.

When welding procedure is established and approved by the Engineer, any proposed change shall be notified in advance to the Engineer for his approval.

4.3. Welding Qualification

The Engineer has the authority to pre-qualify by testing, the welders and the welding procedure.  Only qualified, attested and approved welders and inspectors shall perform, inspect and test the welding works. The standards for training and testing of the welders shall be according to relevant JUS or DIN Standards, respectively.  Written qualification records shall be made available on the Engineer’s request for each welding operator i.e. welder.  Welders to be engaged in welding attachments to pipes 5mm or less in thickness shall be required to demonstrate successfully their ability on contract material.

If, in the opinion of the Engineer, the works of any welding operator at any time appears unsatisfactory, the welder shall be required to pass the appropriate re-qualification test.  All costs of welding process pre-qualification and welders' re-qualification tests shall be borne by the Contractor.

4.4. Welding Equipment and Welding Material

The welding machines, instruments, cables, ground clamps and accessories shall have the capacity adequate for the established welding procedure. The installation, operation and maintenance of those shall be in accordance with the appropriate safety regulations.

Type of electrical welding machines shall be suitable to materials and thickness of joined members, and welding position. All electrical equipment used in connection with the welding operation shall be properly earthed. Arc-welding machines shall be provided with suitable meters to show the welding current and voltage at all time during welding. When using a gas-shielded arc-welding process, means of measuring the gas flow shall be provided.

If weld back purging is applied, the gas mixer machines shall be of sufficient capacity and pipe purging enclosures shall be adequate to the pipe sizes.

The Contractor shall provided calibrated instruments, such as welding micrometer or similar, for measuring the sizes of welds, root gaps, reinforcements of butt welds, concavity and/or convexity of fillet welds, and instruments to measure flow and quality of purging gas (if any).

All instruments and equipment for non-destructive examination and/or testing shall be of the proper range, type and accuracy. Equipment shall be calibrated and certified before any work commences on the project and again at 6 monthly intervals.

The mechanical characteristics of weld metal shall be suitable for the design requirements of the equipment subject to the welding. In general, the yield strength of weld metal shall be at least equal to the minimum in the specification for the base (parent) metal. The chemical composition of the weld metal, including that from fusible insert, shall be compatible with that of base metal. Proposed electrodes shall conform to a particular welding position and type of welding current. The diameter of electrodes shall never be larger than the thickness of the joined metal. When weld a thin metal, an electrode with the diameter smaller than that for successive passes, shall be used for root pass in order to enable full penetration.  Electrodes shall be referred to by a manufacturer’s trade name and classification established by AWS.

Supply of welding electrodes and filler material shall be conducted in the accordance to the progress of the Works. Estimation of required quantity of welding materials shall be justified on the basis of the Contractor’s workshop drawings of elements, or steel structures that shall be subjected to welding. In addition to other technical requirements, shop drawings shall detail each weld to be performed on the site, the type and size of welds, and quantity of weld metal required.

For site erection, all welding electrodes shall be shipped in waterproof containers. Welding rods, which have absorbed moisture in the coating, shall be rejected.

The Contractor shall control the storage and handling of welding material and maintain their characteristics as recommended by the manufacturers. The welding materials shall be stored in dry storage. Special care shall be taken when using electrodes with low hydrogen coatings. This type of electrodes shall be heated at 150ºC minimum for at least 4 hours prior to using.

The Contractor shall perform the test on two main sizes of electrodes used for welding of the equipment. Tests shall be conducted according to the DIN or other approved Standards.

Shielding and purging gases or gas mixtures that have been provided shall be appropriate to the established welding process. When gases are heavier than air, precautions shall be taken to ensure adequate ventilation and extraction.

4.5. Stress Relieving

The welding procedure shall control and minimize distortion and, where necessary, shall include stress relief to minimize residual stress.

When stress relieving is specifically required, such stress relieving shall be done in a furnace and follow approved procedures. Pyrometer charts covering the heat treatment shall be available. A record of the heat treatment shall be supplied to the Engineer.

When necessary, repairs or defects revealed by radiographic examination or otherwise shall be stress relieved again.

4.6. Weld Joint Design, Preparation and Production

All basic types of weld joints, as it is indicated on the relevant Design drawings, shall be performed during construction: butt joints, lap joints, corner joints, tee joints and edge joints.  The types of welds may be stringer or weave bead, groove, fillet or any other types when it is found to be appropriate.  Welds shall be performed in all positions.

The Contractor shall prepare joints for welding, except where pipes to be welded to each other are with pre-fabricated ends. Joints shall be prepared in accordance with either the provisions of this Specification and Tender drawings, or as it is agreed between the Contractor and the Engineer. The Contractor may propose the joint design he considers to be more effective for particular application. Any such proposal or suggestion shall be submitted in advance to the Engineer for his prior approval.

Surfaces to be welded shall be free of all foreign material such as water, scale, slag, heavy rust, grease, coatings, paint, cement, etc., and shall be smooth, uniform and free of defects that could affect proper welding.

Members to be joined by welding may be cut and prepared to required shape and size by mechanical means such as band saw, straight blade, grinder, or any gas or arc cutting. Cut or sheared edges to be welded shall be abraded, and any residual light film of rust shall be removed. Torch cut or air-arc gouged edges shall be ground to remove slag and oxidation. The edges of surfaces to be welded shall be free of visible defects at least 50mm back from the edge of the weld, such as laminations or defects caused by cutting operations.

Special care shall be taken to protect pipes anti-corrosion protective coats during cutting of pipes. A 450 mm wide strip of heat-resistant material shall be wrapped over the top half of the coated pipe on each side of the weld area to avoid damage to the coating. The same protective measure shall be performed during welding.

Welding work shall be properly protected against unfavourable weather condition, and shall not be performed in windy conditions or when welding surfaces are wet from rain, condensation, snow, or ice.  When the ambient temperature is less than 0ºC, preheating shall be required prior to the proper welding method.  When the ambient temperature is less than -5ºC, welding shall be performed only with written permission by the Engineer and according to the proper welding method.

No thermal cutting or welding shall be carried out when the temperature of the base metal within 150mm of the joint or cut is less than +5ºC, or when the temperature is less than +10ºC at any point within 75 mm of the point of welding or four times the pipe wall thickness, which ever is greater. In such case pre-heating for thermal cutting is obligatory. The Contractor shall propose the method of pre-heating in his welding procedures. Pre-heating may be applied by electric resistance heaters, induction heating, oxy-acetylene or other gas torches.

Pre-heating for welding to a minimum pre-heating temperature of 100ºC shall be applied when it is affected by welding component thickness and type of electrode, and when proved by welding procedure.  If pre-heating is necessary, pre-heating temperature shall be maintained within defined area of welding, and periodically checked to ensure evenly temperature distribution around and through the join to be welded.

No water shall be used to expedite the cooling of the welded elements, following the welding.

The Contractor shall provide adequate mechanical means to maintain the specified alignment and root gap during welding. Welded-on bridge pieces are not allowed to be used for these purposes.

Small tacks for positioning of assembly parts during weld jointing are allowed. The maximum length of tack welds shall not exceed twice the thickness of welds or 25mm, whatever is lesser. The throat thickness of tack welds shall be similar to that of root run. Electrodes or filler material used for tack welding shall be of the same type and class as, and of a size not larger than, those to used for completing the first run of weld metal.  Tacks need not to be removed providing they satisfy requirements of approved standard, unless otherwise instructed by the Engineer. Cracked welds shall be completely removed.

All necessary measures shall be applied to prevent damage to base metal by arc strikes which may occur during starting the arc, dabbing electrode while removing the slag from the tip, or may be caused by stray arcing. Strikes that occur shall be assessed and when necessary shall be either ground smooth or filled to restore the metal thickness.

Each pass of weld metal shall be inspected to make sure it is clean before a further pass is applied. Special attention shall be paid to the junction between the weld metal and the fusion faces. All visible deposition faults shall be removed before running a further pass.  When multiple-pass weld is applied, the Contractor shall defined the number of beads (not less than one bead for each 3mm of pipe thickness) and built-up sequence, i.e. order of deposition of beads in the joint, and shall define the interpass temperature below which the previously deposited weld must be before the next pass may be started.

The Contractor shall apply all necessary measures to reduce the heat input to the base metal and control internal stresses, distortion and warping caused by expansion and contraction of joined members. These measures, where applicable, may be as following:

- Proper edge preparation (proper bevelling and adequate spacing) and fitting-up or fixing the joined members using jigs and fixtures.

- Using tack welding, especially on long joint; tack shall be spaced at least 300mm apart.

- Increasing the speed of welding.

- Limiting the number of weld passes.

- Using a chain or staggered intermittent weld (skip weld method), or using a back-step weld method; permissible only when approved by the Engineer.

- Using initially different weld angle (back pull), when anticipating the direction of distortion.

- When pipe joints are to be welded, but thermal expansion joints are not foreseen, the Contractor shall consider appropriate methods to reduce thermal stresses having in mind variation of pipe temperature in the moment of welding and those expected in operation.

On the basis of indoor ambient and fluid temperature variation as it is given in the following table, the Contractor shall propose methods such as shading (if pipes are exposed to sun light before or during welding), or making closure joints at the time when the pipe temperature come near an average value to which pipelines shall be subjected in operation.

| Indoor ambient temperature | -10º C ÷ + 40º C |
| --- | --- |
| Water temperature | +2º C ÷ +30º C |
| Filter backwash air | +87º C, based on ambient temperature of +20º C |
| Service air | +15º C above ambient temperature |

Post-weld heat treatment shall be applied only for weld-throat thickness greater than 35mm. In that case, the heating temperature shall be within the range 580ºC to 620ºC and the time at this temperature shall be 2.5min per millimetre of thickness with a minimum of 30min.

All welds shall be made continuous and watertight. After finishing, welded joints shall be dressed to produce a smooth uniform surface and be free of flux and scale to allow radiographic examination. Cracks in weld and base metal, incomplete fusion, lack of complete joint penetration, weld undercutting and overlapping, and pinholes are unacceptable and shall be repaired.

Welds shall be generally treated so that they shall display good appearance and a surface suitable for painting. Slugs shall be completely removed by using shipping hammer and metal wire brush, accomplished when necessary with power tools and chemical agents. Welded joints shall not be covered or coated until after welding is completed, inspected, repaired (in any) and finally accepted. Structural welds shall be ground and blended to avoid stress raisers, but no welding ground shall be made on the coated section of the pipes.

4.7. Welded Joints in Steel Pipes

The ends of pipes shall be cut or prepared as appropriate, and be free from fins, planar defects, tears and other surface defects, prior to welding.  Cleaning to base metal shall extend for at least 25 mm from the end of pipe on both internal and external faces.  The alignment of abutting pipe ends shall be such as to minimize the internal offset between surfaces.

The Contractor shall submit details of the proposed welding and welding repair procedures, before production welding begins, and test welds using these procedures shall be made by the Contractor under simulated site conditions.

Welders shall only make welds for which they are qualified and approved.

Joints shall be tested using non-destructive techniques, unless it is necessary to use destructive testing to achieve adequate interpretation.

Elastomeric ally sealed joints shall not be permitted unless specified elsewhere in the Contract.

4.8. Pipe to Pipe Butt Joints

Pipe to pipe field butt joints shall be assembled so that seams in adjacent pipe sections or fittings are offset from each other by at least five times the thickness of the thinner of the pipes or fittings being joined.

Matching surfaces of butt joints shall be accurately aligned and retained in position during the welding so that, in the finished joint, the matching surfaces shall not be misaligned by more than (20% of the pipe wall thickness or a maximum 3.2 mm which ever is less)  proposed by an approved standard.

The maximum limits for bore diameter difference and alignment at the bore diameter shall be as defined in an approved standard, or as it is defined in BS 2971:

| Bore diameter mm | Maximum difference in bore diameter (rounded to the nearest 0.5mm) |  | Maximum out of alignment at the bore diameter (rounded to the nearest 0.5mm) |  |
| --- | --- | --- | --- | --- |
|  | With backing ring | Without backing ring | With backing ring | Without backing ring |
| DN ≤ 150 | 1.5mm | 3.0mm | 1.5mm | 2.5mm |
| DN > 150 | 2.5mm | 5.0mm | 2.5mm | 3.0mm |

The butt welding of joints shall include the matching of pipe bores to ensure tolerance limits, if necessary.

Matching of ends shall be effected by use of a suitable expander. When hot expanding is used, the pipe shall be heated to a temperature within the range 900ºC to 975ºC or alternatively to a temperature within the range 450ºC to 650ºC.

After expanding, the thickness at every point in the circumference end of the weld preparation shall not be less than the design thickness for the pipe.  Expansion shall be run out smoothly into the bore at a taper not steeper than 1 in 4.

Before welding, the pipe ends shall be prepared to ensure required shape.

For pipes that are intended to be in axial alignment, the end planes shall be square with the axis of joined members. For pipes that are designed to be out of axial alignment, the plane of joints shall be bisecting the angle of the joined sections.

Butt joints for pipe sections with wall thickness up to and including 3mm shall be square type with root gap 1,5mm – 3mm.  For pipe sections with wall thickness greater than 3mm and up to and including 16mm, butt joints without backing ring shall be single V groove with bevel angle 30º - 40º, root gap 2.5mm – 4.0mm and root face 1.0mm – 2.5mm.   For pipe sections over 12.5mm thick, the butt joints without backing ring  may be  double V groove with bevel angle 37.5º – 45º, respectively 15º - 20º, root gap 2.5mm – 4.0mm and root face maximum 1.5mm. The orthogonal projection of groove face with bevel angle 37.5º – 45º shall be at least 6mm in length.

Circumferential pipe to pipe joints for steel pipe DN150 and greater, shall be welded by metal arc-welding process. Sections of steel pipes smaller than DN150 may be welded with other welding methods.

Single butt joints may be welded from the outside of the pipe or from inside the pipe if the diameter is large enough. The exterior backing rings may be allowed upon approval of the Engineer and, if used, may remain after welding.

If external backing rings are used during welding, the butt joint preparation shall be in accordance with BS 2971.

Welded joints likely to be subjected to dynamic loads or vibrations or to high water velocity shall be ground plane or to a smooth radius. Welding shall normally be carried out by butt jointing with a root run.

4.9. Welding Stainless Steel

The pipes and fittings, as well as other equipment made of stainless steel shall generally be manufactured of austenitic stainless steel, types 304, 304L, 316 and 316L. When welding austenitic stainless steel at the site, the Contractor shall follow the instructions of the manufacturer of the equipment and/or the requirements of this Specification, the applicable and approved standards, and/or approved codes of practice.

Back purging shall be applied, when welding stainless steel pipes. The purging gas to be used shall be argon, helium or nitrogen, or an argon/hydrogen or nitrogen/hydrogen mixture. The root (first) pass shall be made the inert gas tungsten-arc- welding process, and this pass shall insure good root penetration. The inside of the pipe shall be purged with inert gas to prevent oxidation of the underside of the weld during root pass welding. If pipe wall thickness is up to 3/16", the welding shall be completed with the same process. If pipe wall thickness is heavier, the weld, after the root pass, shall be completed by shielded metal-arc welding with covered electrodes, by the inert-gas shielded electrodes, or by the submerged-arc-welding process.

The post-heat treatments of welds are required where service environments tend to be stress-corrosive, or where inter-granular corrosion is a factor. In such cases, the welds shall adequately be heat treated in order to restore expected level of corrosive resistance. The heat treatment procedure shall be in accordance with the instructions of the manufacturer of equipment that might be exposed to corrosive action. If such instructions are not available, the heat treatment procedure shall be agreed between the Contractor and the Engineer.

The Contractor shall carefully examine service and environmental conditions to which the equipment made of stainless steel is designed for, and shall accordingly propose appropriate type of welding filler metal in order to avoid cracking and/or other problems that could arise during welding. The contractor shall submit to the Engineer for approval, the list of proposed type of welding filler metals, i.e. electrodes, or bare electrodes and welding rods. The type of welding filler metals shall be in accordance with AWS and ASTM Specification or similar.

If there is need to weld stainless steel other than austenic, the Contractor shall submit to the Engineer for approval, proposed method of welding that shall include all details related to such type of materials.

4.10. Segmental Bend Joints

Bends shall be of segmental/mitre type, made of separate pieces of pipe cut at an angle and welded together.  All welds in a segmental bend shall be treated as butt welds.  Preparation of segment ends shall be as specified for pipe to pipe and pipe to fitting butt joints.  Numbers of segments, i.e. number of cuts, and bend radius shall be as defined on the reference drawings.  Segmental bend butt joints shall be sound and shall penetrate at all points.

4.11. Branches and Small Bore Connection Joints

Angles between the main pipelines and the branches shall be as defined on the reference drawings.

Branch connections and branch openings in the main pipe shall be cut by machining or thermal cutting. The cut ends shall be dressed by chipping, filing or grinding to remove any roughness.

Preparation and assembly of set-on branches shall be as defined in an approved standard, or as it is defined in BS 2971. The joints shall have the gap which shall be maintained during deposition of the root run.

Small bore connections joints shall be either set-on so that the end surface of connection pipe is in contact with the main pipe surface, or so that the surface of connection pipe is in contact with the main pipe end surface. The fillet weld leg length shall be at least equal to the pipe thickness but in no case less than 8 mm.

The surface of small bore connections ends that is in contact with pipe surface shall be machined flat except where the gap at the flanks would exceed 3mm. In that case the connection pipe ends shall have the contact surface shaped to the contour of the pipe.

4.12. Flange Joints

Depending on type of flanges (welding neck, or slip-on flange), butt, half-open corner or tee joints shall be used when weld the flanges to the pipes.

Welding of neck flanged shall be in accordance with requirements as for pipe to pipe butt welds.

Slip-on flat and hub bed flanges, shall be either "slip-on" welded on pipes (fillet weld on the back side of the flange and corner weld on the front side), or "face and fillet" welded on pipes (fillet weld on the back side of the flange and single-J weld on the front side).

The throat of flange fillet welds shall be equal to the thickness of the pipe but not less than 6mm.  Lap or fillet welds shall have legs of equal size, unless specified otherwise. The minimum size of tee-fillet welds, measured on the leg, shall be 1.5 times the thickness of the pipe, but not less than 6 mm.

Flange single-J welds shall have minimum angle of 20º and minimum radius 5mm. Penetration of single-J welds shall be ranged in accordance with the pipe size.

Before welding, the slip-on flanges shall be fixed to ensure alignment to the pipe axis and to ensure a concentric position to the pipe. Clearance between overlapping surfaces of pipes and flanges shall be as uniform around the periphery as possible.

The clearance between the outside diameter of the pipe and bore of the flange shall not exceed 3.0mm at any point and the sum of the clearances on any diameter shall not exceed 5.0mm.

Overlapping or burning back the inside or outside corner during application of a fillet weld shall not be permitted. The finished fillet weld shall be free of grooves, smooth and with constant section. The faces of fillet welds may be flat to slightly convex.

4.13. Welded Joints in Plastic Pipes

Fusion welded joints in high density and medium density polyethylene pipes shall be made only between pipes having the same physical characteristics. Joints between pipes from different manufacturers shall only be made with the specific approval of the Engineer.  Site fusion jointing shall be made in accordance with manufacturer's instructions.

When solvent welded PVC-U pipes are jointed outside the trench, they shall not be lowered into place until the period recommended by the manufacturer for complete setting of the joints has elapsed.  A pipe section containing a completed weld shall achieve the same strength characteristics as the parent pipe.  Heat fusion jointing of polyethylene pipes shall only be carried out by operatives who have undertaken training in accordance with National requirements. Documentary evidence of successful completion of the training course shall be submitted to the Engineer for approval prior to the operative commencing work on heat fusion jointing.

The ovality of straight polyethylene pipes shall not exceed 2% in diameters up to and including 250 mm, and 3.5% in diameters over 250 mm. The ovality at any section in a coiled pipe after uncoiling shall not exceed 12%.  Coiled pipe shall be re-rounded for electro fusion jointing by use of suitable clamps and/or approved inserts.

5. Pipelines

5.1. Piping Installation

Implementation of the piping installation shall include but shall not be limited to the following works:

- Production and preparation of all supports, including steel supports and concrete bases, as necessary.

- Installation of the supports on the bases, which were prepared for them.

- Preparation of temporary supports, as necessary.

- Installation of piping sections on the supports.

- Installation of all the accessories in the line, including, instruments, etc.

Balancing and levelling of all the lines.

Connection of all the sections to a continuous line, through closure of flanges, welding, cutting, fusion or any other means, according to drawings and the nature of the line.

5.2. Prohibitions in the Installation of the Piping

- Unless specified otherwise, the Contractor shall not drill holes in the piping in order to connect accessories to it, or use connection by insertion, but shall use only industrial accessories such as connectors, junctions, etc.

- The installation of the piping shall be “direct”, such that no stress distortions or cutting of the equipment shall be caused.

- The Contractor shall not cause tension or contraction stress in the equipment to which the piping is assembled because of an incompatibility in length, etc.

- The Contractor shall not attempt to repair or straighten piping that has become bent, is not round or has received any blow during the haulage, installation, etc., unless he notifies the Engineer and acts according to his written instruction.

- The Contractor shall not attempt to fill the piping with water, compressed air, a chemical solution or any other material other than according to the explicit written directive of the Engineer and only in the presence of a competent representative of the Employer.

5.3. General Provisions

Pipelines that are in the scope of mechanical works shall be made of metallic pipes delivered and stacked at the site.

The Contractor shall off load the delivered pipes and stack them at site in bunches according to the manufacturers instructions. The Contractor shall prepare good, levelled, hard standing surface for stacking, accessible to road vehicles, and shall supply enough quantity of strong timbers and wooden battens for supporting the pipe bunches.

Off loading the pipes by lifting device shall be carried out smoothly without snatch. The lifting device shall be of the type to retain the load safely in the event of power failure. If pipes are delivered in bundles, they may be so stacked. During off loading, slings shall be used around the complete bundle. Bundles must not be lifted by their retaining straps. Bundles shall be lowered to the ground before straps are cut.

Individual pipes shall be lifted by the retaining straps and using purpose designed padded hooks. Individual pipes of smaller size may be off loaded by rolling them down a ramp of timber skids extending from the vehicle side to the ground. Steadying ropes shall be used to prevent pipes rolling down at excessive speed and striking other pipes or objects on the ground.

Depending on size and mechanical properties, different types of stacking may be used: square, parallel or pyramidal. Stacking heights depend on allowable stress on the lowest pipes in the stack, the total crane lift available and the facility available to ensure stable stacking. Stacking heights shall never exceed the limits recommended by the manufacturers.

The Contractor shall take care to avoid any damaging the pipes, pipes protective coating or deforming the pipe ends during stacking, internal transportation, handling and installation.

Hanging of pipes during installation shall be in an approved manner in order to avoid damages of pipes lining. Laying the pipes on the supports, levelling and positioning to the adjacent pipe and preparing for welding shall be as accurate as possible. After centering, the pipes shall be spot welded, or hand tightened to the adjacent, wedged to the supports and just after that taken off the slings, ropes or straps.  Pulling of pipes along supports shall not be allowed, except when supports are equipped with sliding paths (shoes). Any damage of pipe linings caused by an improper handling during installation shall be repaired in accordance with the specified requirements.  The stacked pipes, depending on size, shall be 6.0m -12m long, and shall have calibrated ends already prepared for welding.

Cutting of pipes shall be performed by using power driven abrasive wheel disc machine or saw. In general, cutting the pipes with flame is not permitted, except in special cases when an approval by the Engineer must be obtained in advance.

After pipe cutting, burrs and sharp edges shall be removed, and the cut ends prepared for welding. Before welding, ovality of pipes shall be checked.

Pipe cut-offs produced during construction may be welded into the pipeline but shall not be shorter than twice the diameter of the pipe or 600 mm long whichever is the lesser. When a pipe is cut, the cut-off shall be given a suffix number to trace its inclusion elsewhere in the pipeline.

Pipe sections shall be but-welded. Preparation and welding shall be in accordance with JUS standard or another standard approved by the Engineer, and in accordance with specified requirements (STS).

Bolted, flanged joints that facilitate the assembly and maintenance of lines, piping valves and equipment, shall be performed when specified. Unless specified otherwise, depending on type, flange shall be but (necked flange), overlap (slip-on), and/or fillet (flat flanges) welded to the pipeline. Stainless steel pipe flange shall be the loose type. Flange bolt holes shall straddle the natural pipe centre lines, and shall match the orientation of mating flanges of equipment.

A uniform distribution of the pressure over the gasket circumference is necessary for satisfactory sealing. To achieve this, the manufacturer’s installation instructions must be strictly followed. Whenever the manufacturer misses to submit such instructions, the bolts shall be tightened in the following sequence:

- Identified flange, bolts, nuts and washers shall be in accordance with the General Technical Specification or Specific Technical Specification

- Flanges, bolting material and gasket are clean and free of damage

- Bolts and nuts are properly lubricated

- Torque and/or tensioning tools are calibrated

- Pull the flanges together using flange pullers until there is gap of approximately 50-75 mm

- Using caulking or similar tool, insert gasket between flanges; gaskets shall not protruded into the free area of the pipe

- Continue to pull up the flanges using the flange puller until the flanges are firmly together and the gasket seated

- Insert the stud bolts

- Hand tighten all nuts

- Tighten two bolts diametrically opposite each other (two bolts practitioners working simultaneously on diametrically opposite bolts are usually requires for sizes with 12 or more bolts)

- Tighten another pair of bolts approximately 90º further round the circumference

- Continue until all bolts have been tightened accordingly to manufacturer’s instructions regarding bolt torque, stress or stretch

- Complete further tightening circuits in the recommended sequence, as instructed by the manufacturers

- Check the flanges gap by taking measurements at 12, 3, 6 and 9 o’clock position

The joints must be precisely bolted, with regard to achieving an accurate preload defined by the manufacturers. Insufficient or excessive preload, caused by an inaccurate tightening method, may cause the bolted joint failure. Method of tightening shall be elaborated in the method statement.  The preload of bolts must be controlled by one of the following method:

•	torque control tightening

•	angle control tightening

•	yield control tightening

•	bolt stretch method

•	heat tightening use of tension indicating methods

Final bolts tightening shall be performed with precision torque or tensioning tools. Torque tools may be manual, pneumatic or electrical dial torque wrenches or spanners. Bolt tensioning equipment may be pneumatic or hydraulic, and shall include tension control that interrupts incoming flow to power tool to stop tension and automatically shut the tool once the bolt has reached required tension.  If bolts are tensioned, an estimated relaxation factor must be taken into account, to obtain an extra load that is transferred from the tensioner to nuts. Extra load applied, enables bolts to relax down with required tensioning.  Torque and tensioning equipment must be periodically monitored and calibrated by control instrument.  The bolts shall be re-tightened after commissioning.

During assembling pipe flange joints, gaskets shall never be re-used, since not enough resilience is left in gasket material to give a leak-proof joint when compressed a second time.  Bolting practitioners shall be well qualified personnel capable to demonstrate their proficiency in the preparation and assembly of bolted flange joints in accordance with an established method statement.

Additionally, the pipe work shall include treading the pipes (tubes), and manufacturing on site pipe fittings (mitre bends, tees, branches, puddles).

Threaded joints shall be in accordance with relevant piping class. The use of threaded joints is limited to instrument connections and small size valves.

A mitre bends shall be made at site, in the Contractor’s workshop. The bends shall be, depending of angle, composed of two or more straight pipe sections matched and joined on a line bisecting the angle of junction producing the change of direction.

The wall thickness of mitre bend sections shall be greater then the thickness of the straight pipe by the factor

R−0.5rR−r , where:

R – equivalent bend radius (min. 1.5 time pipe ND, if not designated on relevant drawings) and

r – inside pipe radius.

The mitre angle shall be limited to 11.15º for a 3-section mitre.

The Contractor shall produce all branch connections that connect branch pipes to the main pipes. When it is necessary for the purpose of installation accuracy, or convenience, the branch connection shall be performed in the form of a tee piece. If a tee piece could be exposed to severe operating conditions, or it is of shape that may impose the high stress contraction, such piece shall be strengthened by collars.  Merging or diverging angle of a branch shall be as it is designated on the relevant drawing.  The Contractor shall prepare shop drawings of all mitre bends and tee pieces. These drawings shall be subjected to approval by the Engineer.

The number of blind flanges and counter flanges (if any), and bolting and sealing elements that are going to be used for the pressure testing of piping systems, shall be determined by the Contractor, who shall be fully responsible for supplying of such items. Quick-acting blinds are allowable if appropriate for particular application.

All pipes shall be mounted on pipe supports in an approved manner. All necessary slings, saddles, structural steelwork, fixing bolts, and all other attachments shall be manufactured by the Contractor, from the stocked material supplied by the Supplier.  All brackets or other forms of support shall be rigidly built up of riveted or welded steel sections. The structural steelwork has a preference over castings.

The Supplier shall show the location and full details of all embedded components on his drawings and shall be responsible for the completeness and accuracy of his drawings and the information supplied to the Contractor. Anchorages to be embedded in primary concrete shall be installed by the Contractor according to the Supplier's design i.e. approved foundation drawings.

Any steelwork, which is to be built into the concrete foundations, shall not be painted or coated unless otherwise approved or specified.

Piping within buildings shall be adequately anchored and supported from the floor, wall beams or ceilings. Supports from the floors shall be by approved saddle stands or concrete piers. Pipe saddles shall be shaped to fit the pipe which shall be supported and shall be capable of adjustment. Concrete piers shall be so designed that they shall conform accurately to the bottom one-third to one-half of the pipe. Piping along walls shall be supported by approved wall brackets with attached pipe rollers or saddles or by wall brackets with adjustable hanger rods. Approved rod hangers of a type capable of screw adjustment shall support piping supported from the ceilings.  In all cases pipe supports or hangers or brackets shall be placed as to prevent the pipes sagging.

For water tanks into which the water is transported or from which the water is transported, the Contractor shall install the pipes and pipelines so that their inlet and/or outlet cross sections are 30 cm away from the water tank internal wall plain.  The Contractor shall then weld blind flanges onto these pipe extensions, for hydrostatic test purposes.  After a successfull pipeline welding test, the Contractor shall cut said extensions so that the pipe inlet/outlet cross sections are aligned with the wall plain.  The Contractor shall smooth out the pipe edges after cutting and fix any possible damages to the anticorrosive coatings applied on the inside surface of the pipes (all according to the sections of this GTS regarding pipe cutting, pipe welding and anticorrosion).

5.4. Cutting Pipes

Pipes shall be cut by a method which provides a clean square profile, without splitting or fracturing the pipe wall, and which causes minimal damage to any protective coating.  Where necessary, the cut ends of pipes shall be formed to the tapers and chamfers suitable for the type of joint to be used, and any protective coatings shall be made good, and the ends sealed.  Where ductile iron pipes are to be cut to form non-standard lengths, the Contractor shall comply with the manufacturer’s recommendations in respect of ovality correction and tolerances to the cut spigot end.  Where concrete pipes are cut any exposed reinforcement shall be sealed with an epoxy resin mortar.  Full surround clamps shall be used when cutting PVC-U pipes.

5.5. Pipe work and Valves Support

All necessary supports, including structural steelworks, foundations, hangers, saddles, sliding shoes, slings, fixing bolts, foundation bolts, fixing and anchor points and all other attachments, shall be installed to support the pipe work and its associated equipment in an approved manner. Valves, meters, strainers and other devices mounted in the pipe work shall be supported independently of the pipes to which they connect.

All brackets or other forms of support, which can conveniently be so designed, shall be rigidly built up of steel sections by riveting or welding, in preference to the use of castings.  No point of passage of pipes through floors or walls shall be used as a point of support, except with the approval of the Engineer.

All brackets and fixings shall, as a minimum, be painted.

5.6. Hangers and Supports

Pipes shall be installed on supports and hangers. Hot water pipes shall be installed so as to allow free expansion, without damaging the Isolation. Fixing supports on walls and ceilings shall be made with split bolts. Unless specified otherwise, hangers or supports shall be spaced not to exceed the following distance data, while minimum two hangers or two supports shall be provided in each case.

5.7. Steel Pipes

Unless instructed differently by the Engineer or shown differently in the technical drawings, the Contractor shall use the following for steel pipe supports

Vertical Pipes - 3.0 meters, one support minimum at each floor.

Horizontal Pipes (for standard wall thickness pipes, sagging 0.254 cm and strain 10,342 kPa):

| Nominal diameter (cm) | Distance (m) |
| --- | --- |
| 2.54 | 2.13 |
| 3.81 | 2.74 |
| 5.08 | 3.05 |
| 6.35 | 3.35 |
| 7.62 | 3.66 |
| 8.89 | 3.96 |
| 10.16 | 4.27 |
| 12.70 | 4.88 |
| 15.24 | 5.18 |
| 20.32 | 5.79 |
| 25.40 | 6.71 |
| 30.48 | 7.01 |
| 35.56 | 7.62 |
| 40.64 | 8.23 |
| 45.72 | 8.53 |

5.8. Fixed Posts

Fixed posts shall be provided in the pipeline between each two-expansion joints, where indicated.  Fixed post shall anchor the pipe to a structure element to prevent its movement at that location during expansion.

5.9. Sleeves and Passages

Unless specified otherwise, pipe passage through floors, walls, ceilings or roofs shall be within sleeves made of PVC pipes cast or fixed in construction. Sleeve ends shall be cut straight and smooth and equipped with rosettes. Sleeves passing through platform shall protrude of final floor surface in compliance with the drawings or instructions.

Pipes passages through external walls, the gaps between the wall and the sleeve shall be filled with sealing material of single component and dual component elastomeric sealant for use in buildings.

All pipelines shall be laid and fixed in such a manner that non-permitted vibrations are prevented. Welding of the pipelines to their fixtures shall not be allowed.  Deviation of the pipes from the straight line must not exceed 0.2 to 1%.

5.10. Cleaning the Equipment and Associated Pipelines

Piping associated with pumps and compressors shall be thoroughly cleaned before equipment is put in operation, in order to ensure trouble-free operation and to avoid damages due to deposits, dirt, foreign matter (welding slag, etc.).  Cleaning shall be performed with water and/or air, and/or using polyurethane swabs.  This requirement shall be considered and defined for each particular installation, following the manufacturers’ recommendations.

The Contractor shall provide all means necessary for cleaning purposes and shall give the proof that the flow during water/air blowing is adequate. During blowing, the condition shall be at least 80% of design pressure and flow.

Cleaning of pipeline shall always be performed without any back-pressure, for about 10 min.  Approx. 0.3 to 0.5 m from the end of the pipelines, a baffle perforated plate shall be arranged.  After cleaning, the baffle plate shall be inspected to locate the highest concentration of impressions of projected particles on the plate. The number of impressions on 1 cm2 in the area of highest concentration shall be counted. The piping is considered clean if fewer than two particles impressions in the 1 cm2 area are shown. The cleaning shall be repeated after the piping is demonstrated to be clean.

Air blowing is preferred to be done with hot air, since thermal expansion and contraction are necessary to remove welding slag.  In that case the following precaution measures must be undertaken:

- The manufacturers shall be consulted regarding maximum operating temperature to which equipment component may be exposed (pipelines and valves protective coatings, valves and flanges gaskets, valves sealing elements, etc.).

- The section of a pipeline that is intended to be blown through with hot air, must be carefully examined for thermal loadings.

For cleaning of equipment rotating parts, bearing houses, etc., a suitable non-flammable safety solvent shall be used. The use of paint thinner, gasoline and similar liquids is not permitted because of their adverse effects on internal painting, O-rings, gasket, etc. In general, the use of volatile inflammable hydrocarbon solvents is prohibited.  After solvent cleaning, parts shall be preserved with suitable preservation oil.

6. VALVES

6.1. General

After the Contractor receives the valves on the site due to the procedure specified in General Technical Specifications, he shall be fully responsible for keeping the valves in good condition. Storage, handling, and installation shall be performed strictly in accordance with the Contractor’s Method of Statement, which shall be based on the Supplier’s instructions and requirements specified in General Technical Specifications and/or Specific Technical Specifications.

6.2. Unloading and Storage

The valves shall be unloaded, transported and stored on the manufacturer’s original storage and material handling equipment, e.g. pallets. After checking the equipment, the Contractor shall restore protective coverage (cardboard, plywood, plastic plates, thermo-welded plastic bags with desiccant, protection caps and plugs onto threaded holes, etc.) to prevent damage to seat  and flange faces, and interior of the valves.

If valve’s actuator moves during checking, the Contractor shall move it back to the initial position. In general, vales are supplied with the actuator in closed position to prevent damage of seats, but wafer type butterfly valves are supplied with the disc positioned at 10º opened.

The valves shall be stored indoors. Indoor temperature shall preferable be +5ºC to +30ºC. During storage period the Contractor shall provide all other suitable measures against contamination, frost, humidity and corrosion. The valve flanges generally are coated with an anti-corrosive which can easily be removed, and the valves inner surface are protected with synthetic silicone-free anti-corrosive for long-term preservation. For storage period longer then 12 months the Contractor shall provide additional preservation and protection measures if so  recommended by the manufacturers, and shall open and close the valves once every 3 months.

During unloading, transportation, storage (and installation), the valves shall not be thrown, dropped or subjected to hard impacts. The centres of gravity of the valves and the entire packaging unit must be taken into consideration. Only transportation lugs provided on the valves and/or packages shall be used during unloading and loading the valves from vehicles.

While hoisting valves for installation, the Contractor shall make sure that lifting tackle is properly attached to the valve, and not to movable components such as hand wheel, gear unit, actuator, by-pass line, instruments, or other attachments.  Straps must be tied around the valve body.  To hold the valve in vertical installation position and avoid tilting, two straps shall be routed to the lifting hook between the hand wheel arms. If required by the valve’s centre of gravity, a third strap shall be used to prevent the valve from flipping over (usually used for gate valves with ND ≥ 300). The third strap also serves to keep the valve in horizontal position. The third strap shall be tied to the valve neck flange, bonnet flange or stem protection guard.

6.3. Safekeeping

To keep the proper and intended use of the valves in the course, the following instructions must be complied with:

- before transportation from the storage to the place of installation, the valve intended to be installed must be clearly verified by comparing TAG number on the valve body/package nameplate (marking) to that designated on P&I diagram; otherwise, the valve may be exposed to service and operating conditions for which it has not been designed

In order to avoid injury from uncontrolled movement of movable parts, the following precaution measures shall be taken into account during transportation and installation:

- protective elements must not be removed until immediately before installation

- transport locks must only be removed after installation

- personnel must not reach into the valves during valves installation

- centres of gravity must be taken into consideration

- movable parts such as  remote actuation components must be locked by suitable means; any locks previously removed must be re-installed

- protruding or projecting parts of the valves must not be used as footholds in order to prevent flipping over and falling of equipment

To prevent hazard to persons or the environment, or failure of the valves to operate due to incorrect installation position, the following instructions must be followed before commencing to installation:

- the relevant health and safety regulations and pertinent legal provisions must be adhere to

- the layout position, flow direction, and orientation of the valve must be in accordance with relevant drawings, P&I diagram and the manufacturer’s data; during installation, these documents must be adhere to

- before installation, the valve must be inspected for in-transport damage

- before installation, the valve must be once again checked for its designated use

- the valve must not be used as anchorage points; the valve shall be installed after adjacent pipes and fittings are installed, properly supported, and inspected

- where foreseen, the valve permanent support must be prepared

For proper installation the following instructions, in addition to the manufacturer’s instructions, must be met:

- protective elements must not be removed until immediately before installation

- damage parts must not be installed

- make sure that there is no foreign matter, contamination, desiccant, etc. inside the valve

- the mating flanges must be clean and undamaged

- the mating flanges must be in planes  that are normal to the pipeline axis, and  properly centered

- the valve flanges must be clean

- the flange gasket (where applicable) must be properly centered; for this purpose suitable tools must be used

- when connecting the valve to adjacent, only the flange bolt holes provided by the manufacturer must be used

- all flange bolts must be used

- when connecting the valve to the mating flanges, the tightening torques specified by manufacturer must be complied with

- when tightening the bolts in final sequence, only spanners or wrenches with torque dial instrument may be used

- bolt tightening sequences must be performed in accordance to manufacture’s instructions

- where the permanent valve support is foreseen, the tightening of valve to the adjacent fixed mating flange (pipe flange) shall be performed while the valve is hanged on the lifting device; after tightening, wedges and shim strips shall be inserted between valve foots and support; in no case the tightening force shall be used to pull the valve to the adjacent flange while the valve is laid down to the support

6.4. Installation

During installation, special care shall be taken when wafer type butterfly valves are being installed. The valves of this type are designed for use with standard flanges with uniform face. Proper alignment of wafer type valves between flanges is critical to good performance of the valve, both sealing (on faces and valve disc) and operating reliability.

In addition to foregoing general instructions, the following shall be taken into consideration:

- no gaskets are required as wafer type valves have melded liner that serve  the function of a gasket

- align the piping and than spread the pipe accessory (wafer valves are always to be installed in pair with a dismantling joint) a distance so as to permit the valve body to be easily dropped between the flanges without contacting the adjacent flanges

- check to see that the valve disc has been positioned to a partially open position, with the disc edge about 1/4" to 3/8" from the face seat, approximately 10º open; this result that no undesirable initial seating/unseating torque is applied which protected the disc edge and lining

- insert the valve between the flanges, taking care not to damage the seat faces

- valve must always be picked up by the locating holes (or lifting lugs), or by using a nylon sling on the neck of the body; the valves must not be ever picked up by the actuator or operator mounted on the top of the valve

- place the valve between the flanges, center it, and than span the valve body with all flange bolts, but do not tighten the bolts

- carefully open the disc to the full open position, making sure the disc does not hit the adjacent pipe internal diameter

- systematically remove jack bolts or other flange spreaders, and hand tighten the flange bolts in sequence as per manufacturer’s instructions

- very slowly close the valve disc to ensure disc edge clearance from adjacent pipe flange internal diameter, and than open the disc to full open and tighten all flange bolts per manufacturer’s specification

- repeat a full close to full open rotation of the disc to ensure proper clearance

If manual, pneumatic or electric actuators are delivered separately of the valves the following notes shall be applied to the installation:

- verify that the valves and the actuator are both in the same position (both open or both closed); normally the actuator is mounted with its long side parallel to the pipeline

- apply a light coating of grease to the inside of the actuator output bore before installing the actuator on the valve; this shall allow the actuator to be more easily removed from the valve stem even after years of service

- if stem adapters are required to match the actuator output bore to the valve stem, apply a light coating of grease to the inside of the stem adapter as well as the inside of the actuator output bore

- some stem adapters are kits consisting  of multiple components, and may contain spacer that look like stem adapters, but are designed to keep the stem adapters in place during operation of the actuator; verify that all stem adapters and spacers are installed in the proper position and sequence

- if keyed stem adapters are used, the key must be held in the keyway so that it shall not work loose during operation of the actuator; the key may be retained by any of several methods

- if mounting studs are used instead of bolts, thread the studs completely into the actuator before placing the actuator on the valve; this assures that the full strength of the connection is achieved

- while the mounting bolts are only finger tight, cycle the actuator fully open and fully closed to verify proper alignment on the valve

- tighten the mounting bolts or nuts in a diagonal pattern to evenly distribute stress in the bolts

- check the travel stop settings; although the travel stops are set for 90º of travel at the factory, each installation is different so they shall be checked and eventually adjusted before putting the valve in service, specially if valve application requires a few degree over or under travel at ends of rotation (if valve application dictates that valve actuator have more that 5º of travel adjustment then actuator shall be equipped with extended travel stops in the end caps.

7. Painting, Colouring and Corrosion Protection

7.1. General

7.1.1. Scope and requirements

The Contractor shall ensure that, after completion of erection, all equipment has received suitable preparation followed by a suitable protection system.  All surfaces of equipment shall be protected against corrosion and/or erosion with the exception of stainless or corrosion-resistant material or where surface is required to be clear for operational purposes i.e. at glands, bearings etc.  The paint protection system of any item of equipment shall be obtained from the same manufacturer and applied strictly in accordance with the manufacturer's instructions and requirements.  All machined, polished or bright surfaces, both external and internal, shall be afforded suitable and adequate protection against corrosion, damage and deterioration.

The Contractor shall also perform anti-corrosion protection on, and shall paint all equipment that is not shop protected and/or painted. This mainly refers to pipe fittings and supports, as well to other metal works to be done at the site (steel platforms and coverage, hand rails, fences, ladders, etc.).

As a rule, the application of the first priming coat shall follow immediately after the surface preparation. No coating, whether prime or finish, shall be applied before machining, inspection, assembly, and testing of the equipment. This implies that mechanical or chemical surface preparation for the application of protective coatings may not take place prior to machining, field assembly and testing. Exceptions to the rule may be granted by the Engineer on special request if duly justified for manufacturing purposes.

Thus, if authorization for some equipment is granted to perform the surface preparation prior to machining, inspection, field assembly and testing, a temporary protection shall have to be utilized which shall not impair proper inspecting and satisfactory bond to the surface of final priming and coating.

The first-class quality protection against corrosion shall require the fulfilling of two essential conditions. Firstly, the surfaces shall be thoroughly cleaned before application of prime coating in order to make sure that the prime non-porous coatings shall adhere to the steel surfaces.  Secondly, to make sure that the first-grade prime and finish coatings shall adhere to the steel surfaces and to the prime coatings respectively. All coatings, prime and finish, shall be of adequate and uniform thickness and shall produce non-porous and elastic finish films.

In order to provide durability of protection against corrosion, all observed mechanical damages of coatings, which can be caused during erection or operation of equipment, shall be immediately remedied and made good.

All paint materials shall be stored and applied strictly in accordance with manufacturers' instructions.  Site painting shall not be carried out unless the surface to be painted is dry and has undergone surface preparation as instructed by the paint manufacturer to ensure a good and uniform "key" onto the existing protective finish.  Paint shall not be applied under adverse conditions.  Air temperatures shall be above 5°C and relative humidity less than 55% or as otherwise specified by the paint manufacturer.  If these conditions cannot be achieved, a special painting system may be applied provided full details of the system are approved by the Engineer.

The Contractor shall ensure that, for the materials specified, application conditions are in accordance with the specification and manufacturer's instructions, paint only being applied to surfaces that have been cleaned and prepared in accordance with these instructions.  Where local climatic conditions are such that the specified requirements are difficult to achieve the Contractor shall provide temporary protection.  No manufacturer's name plate identification, vented filler plugs in gearboxes or grease nipples shall be painted over.  The dry paint film thickness shall be measured by Elcometer.  Surfaces shall be adequately degreased before applying any coating, then pre-treated with a brush application of etch primer or T wash.

7.1.2. Finish

The following table gives the minimal acceptable finish system for different types of equipment.

Further detail requirements for specific items of equipment are given in the detail specification and this takes precedence over any requirement stated here.

| Hand railing, walkways and steel structures installed outside buildings | Hot dip galvanized |
| --- | --- |
| Hand railing with controlled environment | PVC coated |
| Steel surfaces other than pipework in damp or wet environment | Zinc rich epoxy or zinc spray followed by 2 part epoxy top coat |
| Surfaces exposed to direct sunlight | Primer coating system appropriate for base material and environment followed by top coat of epoxy micaceous iron oxide |
| Nuts, bolts, washers and other small hardware | Hot dip galvanized or zinc electroplate |

7.1.3. Toxicity and Bio-hazardous Issues

Substances and products used in the Works which may be applied to or introduced into water which is to be supplied for drinking, washing or cooking shall not contain any matter which could impart taste, odour, colour or toxicity to the water or otherwise be objectionable on health grounds.  All coatings applied to any part of equipment in contact with water to be used for drinking, washing or cooking shall be certified to be used in the food industry, to be non-toxic, non-carcinogenic, shall not impart taste, odour, colour or turbidity to the water or foster microbial growth.  To avoid the possibility of the presence of carcinogenic poly-aromatic hydrocarbons, all bituminous paints and coatings must be manufactured from petroleum or asphalt bitumen and not from coal tar bitumen.

Lead based paints shall not be used.

7.1.4. Metal Paints

Steel subject to hydrogen embrittlement through galvanizing shall not be used.  All iron and steelwork to be painted shall be blast cleaned according to Swedish Standards SIS 99 00 - 1867, A-C, Sa 2 1/2.  Following blast cleaning, steel surfaces shall be pure zinc metal sprayed where specified.  Aluminum structures and fittings shall not necessarily be painted.

7.1.5. Cathodic Protection

Cathodic protection of the steel-welded pipeline shall be envisaged as an additional protection.  The system of Cathode protection shall be proposed in the Electrical Works chapter of the General Technical Specification.

The Contractor may propose another type, number and thickness of coats to be applied. The Engineer may approve the proposal. The characteristics of proposed protection materials shall be such as to suit best the intended purposes of protection. The materials shall be produced in the factories of well-recognized manufacturers.

7.1.6. Warranty

The warranty for the good quality of the protection against corrosion shall be granted for a period of 10 years after Taking Over. Within the warranty period, the degree to which the corrosion processes have advanced must be within the references value of 3/Re 3/, as per European Scale for assessment of corrosion proof coatings, issued by the European Association of the Manufacturers of Protective Coating Agents and Painting Dyestuffs.

7.2. Reference Standards

Protective coatings shall comply with BS 5493 “Code of practice for the protective coating of iron and steel against corrosion”, except as otherwise specified in this section.  For coatings designed to BS 5493 exterior conditions shall be assumed to be “polluted inland” conditions and the interiors of buildings shall be assumed to be "frequently damp or wet" except for control rooms.  The thickness of coatings stated in this section of the specification is the minimum allowable thickness as defined in Clause 19 of BS 5493.  Where available paints do not provide dry film thickness as specified, additional coatings shall be applied.  Protective coatings for surfaces of tanks and other equipment in contact with chemicals or otherwise in conditions not foreseen in this section of the specification or in BS 5493 shall be suitable for those conditions and shall be the subject of design submissions supported by evidence proving satisfactory experience of the proposals elsewhere.  Where dissimilar metals are in contact, the Contractor shall provide insulation to prevent electrochemical corrosion.

Unless otherwise specified or approved by the Engineer, painting and protective coatings, including surface preparation, shall comply with the relevant Reference Standards listed below:

Standard

JUS C.A1.556	Protection against corrosion – testing of electroplated coatings

JUS C.A6.001	Protection against corrosion – Electroplating and related processes

JUS C.A6.005	Protection against corrosion – Metallic and other non-organic coatings –

definitions and conventions concerning the measurement of thickness

JUS C.A6.033	Protection against corrosion – Metallic coatings - 			measurement of coating thickness – Coulometric method by anodic dissolution

JUS C.T7.100	Protection against corrosion – Metallic coatings and the	coatings consisting of

compound of the surface metal - definitions and designations

JUS C.T7.301	Preparation of steel substrates before application of paints and related products –

Visual assessment of surface cleanliness – Rust grades and preparation grades 		of uncoated steel substrates and of steel substrates after 	overall removal of previous

coatings

JUS ISO 8502-3	Preparation of steel substrates before application of paints and related products –

Tests for the assessment of surface cleanliness –

Part 3: Assessment of dust on steel surfaces prepared for painting (pressure-

sensitive tape 	method)

JUS ISO 8502-4	Preparation of steel substrates before application of paints and related products –

Tests for the assessment of surface cleanliness –

Part 4: Guidance on the estimation of probability of condensation prior to paint

application

JUS C.T7.311 – 	Various Standards regarding the actual anti-corrosive JUS C.T7.397

coatings (primers, first coat, top coat, second coat etc.)

BS 245	Mineral solvents for paints and other purposes.

BS 729	Hot dip galvanized coatings on iron and steel articles.

BS 1224	Electroplated coatings of nickel and chromium.

BS 1336	Knotting.

BS 1387	Screwed and socketed steel tubes

BS 2451	Chilled iron shot and grit.

BS 2569	Sprayed metal coatings.

BS 2989	Continuously hot-dip zinc coated and iron-zinc alloy

coated  steel strip, sheet and plate.

BS 3416	Bitumen-based coatings for cold application, suitable for use

in contact with potable water.

BS 3698	Calcium plumbate priming paints.

BS 4129	Welding primers and weld-through sealants, adhesives 	and 	waxes for

resistance welding of sheet steel.

BS 4147	Bitumen-based hot-applied coating materials for protecting iron and steel.

BS 4652	Metallic zinc rich priming paint (organic media).

BS 4756	Ready mixed aluminium priming paints for woodwork.

BS 4764	Powder cement paints.

BS 4800	Paint colours for building purposes.

BS 4921	Sherardised coatings on iron and steel.

BS 5252	Colour co-ordination for building purposes.

BS 5358	Solvent-borne priming paints for woodwork.

BS 5493	Code of Practice for protective coating of iron and steel structures against corrosion.

BS 6044	Pavement marking paints.

BS 6150	Code of Practice for painting of buildings.

BS 6900	Raw, refined and boiled linseed oils for paints and varnishes.

BS 6949	Bitumen-based coatings for cold application, excluding

use in contact with potable water.

BS 7079	Preparation of steel substrates before application of paints and related products.

CP 3012	Code of Practice for cleaning and preparation of metal 	surfaces.

7.3. Submissions by the Contractor

7.3.1. General

Submissions which the Contractor is required to make in relation to painting and protective coatings shall include, where relevant, those listed below.

7.3.2. Schedule of paint systems and protective coatings

The Contractor shall prepare a detailed schedule for the complete Works which shall contain the following information:

- System reference

- Type of surface

- Component or section of the Works

- Environment of item

- Surface preparation

- Paint system or protective coating to be applied

- Name of coating manufacturer

- Brand name and reference number for each coat to be used

- Color of finishing coat stating the Munsell system color notation

- Proposals concerning place of application and detailed method of  application of each coat, including information on equipment to be 	used

- Wet film minimum and target thickness for each coat

- Dry film minimum and target thickness for each coat

- Density of paint for each coat and coverage of paint per unit volume.

The schedule shall be accompanied by manufacturers' data sheets for each coat, including technical description of paint, and the British Standard (BS 4800) shade.  The work detailed on the schedule shall meet the requirements specified or otherwise required by the Contract.  Where practicable, the schedule shall be in the format of the specimen schedule of paint systems and protective coatings included at the end of this Section.  The schedule shall be subject to the approval of the Engineer.

7.3.3. Record sheets

For each section of steelwork, the Contractor shall provide a numbered record sheet and continuation pages in duplicate on which the progress of each operation shall be recorded from the initial state of the steel before cleaning through to final inspection.

All relevant data shall be recorded including:

- Regulations for technical steps and conditions for corrosion protection of steel structures - Official Gazette No. 32/70;

- JUS Standard C.T7.2063/1994 - metal coatings of tin aluminum and lead, applied by method of metal spraying;

- JUS Standard H.C.8.050/68 - inspection methods for checking coating materials for railway vehicles and steel structures.

- reference to identify the steelwork precisely;

- date;

- weather conditions (or ambient conditions in a workshop);

- preparation, coating or repair being undertaken;

- area coated and quantity and type of materials used;

- details of tests and measurements taken;

- delays and causes, faults observed and corrections made.

There shall also be space for comments or confirmation by the Engineer who shall receive one copy not more than 24 hours after the work is completed.

7.4. Workmanship

Paint shall be supplied from the Contractor's paint store to the painters ready for application.  Any addition of thinners shall be made in the store under supervision and up to the limit detailed on the appropriate manufacturer’s paint data sheet, for the particular method and conditions of application concerned.  Paint shall be thoroughly stirred before and during use, and shall be strained as and when necessary.

Paint shall be applied only when the ambient temperature is above 5oC and less than 40ºC, and when the relative humidity is below 55%.  Surfaces to which the paint is applied shall be dry and shall remain free from moisture until the coating has dried or cured sufficiently to avoid effects harmful to the subsequent appearance or satisfactory protective behavior of the paint.

Application of paint shall be by one of the following methods, the choice being the Contractor's unless one particular method is specified or is recommended in the manufacturer's instructions for use of the paint:

-	brush

-	air pressure spraying

-	airless spraying

Paints with suitable flow-out properties may be applied to large flat areas by mohair sleeved rollers.  Rollers shall not be used under other circumstances or for the application of paints containing micaceous iron oxide pigments.

Each coat shall be allowed to dry, be rubbed down and be cleaned as necessary before application of any subsequent coat of paint.

Brushes, tools and equipment shall be kept in a clean condition and surfaces shall be clean and free from dust during painting.  Painting shall not be carried out in the vicinity of other operations which might cause dust.  The final coat shall be uniform in colour and free from brush marks, runs or other defects.

The Contractor shall not dispose of solid or liquid wastes from painting work down any permanent sanitary fittings, sinks or drains and a non-inflammable portable container shall be provided and used for this purpose.

The Contractor shall take every precaution to protect newly painted surfaces from damage by any cause including wind blown dust.  Precautions shall include warning signs, barriers and covers.

7.5. Preparation of surfaces for painting

7.5.1. Protection of surfaces

All necessary precautions shall be taken by the Contractor before the commencement of any painting activities to ensure that no damage or disfigurement of any kind is caused thereby to any part of the Works.  If in the opinion of the Engineer the precautions taken are inadequate the Contractor shall make all such improvements as the Engineer directs.

The Contractor shall exercise particular care not to apply paint to any surfaces not intended to be painted and shall promptly and thoroughly remove any paint applied to such surfaces.  All floors and surfaces liable to damage or spillage shall be protected with dust sheets.

The Contractor shall remove all ironmongery and door furniture before painting work commences and re-fix all items on completion of the painting.

The Contractor shall regard the preparation of surfaces to be painted as work of fundamental importance, the object being to ensure the production of sound, clean, smooth and dry surfaces.  The preparation shall have no detrimental effect on the substrate to be painted nor shall it be prejudicial to subsequent painting operations.

To obtain the first-class quality and durability of protection against corrosion the surfaces of the steel structures shall be thoroughly prepared before application of the prime coat.

Preparation of the surfaces shall be carried out by degreasing and sandblasting.

7.5.2. Degreasing

The surface of structures, which are greased during fabrication or transportation, shall be degreased. Degreasing shall be carried out with tricolor-ethylene (C2HCl3) applied with brushes and clothes, and then well rubbed in. The surfaces shall be rubbed in until all grease is dissolved and eliminated. After being degreased in such a manner, the surface shall be wiped out with dry clean cotton clothes.

7.5.3. Sandblasting

Sandblasting shall be carried out until all impurities, Ferro-oxide, scale, slag and any other mechanical impurities are removed. If the thickness of layers of scales and slag left after rolling or welding is considerable, then they are recommended to be removed and eliminated by hammering. All depressions in sandblasted surfaces shall be free from any traces of Ferro-oxide and impurities.

The sandblasting is carried out using special compressed air apparatus.  The nozzles shall be positioned in such a way that the sand jet and the surface to be cleaned close an angle of about 45o.  The distance between the nozzles and the surfaces to be sandblasted shall be about 50 cm.  Prior to the application of coating, sandblasted surfaces shall be blown clean with filtered dry air.

Since the sandblasted metal surfaces are very active in respect of oxidation, they shall be coated with the prime coat as soon after sandblasting as possible, but not later than within 8 hours. If the ambient air is saturated with humidity, the prime coat shall be urgently applied.

If the welded joints of the equipment are not ground and if the welds are uneven, such welded joints, after receiving two prime coats, shall be coated once again in order to ensure formation of a non-porous layer (film) of prime coat in such uneven spots.

Immediately before application of the first prime coat, the quality of cleaning of sandblasted surfaces shall be thoroughly controlled. If all the pores are not free from impurities and Ferro-oxide, the sandblasting procedure shall be repeated in order to obtain a fine, uniformly and clean surfaces capable of perfectly adhering to prime coats.

Well sandblasted surfaces shall satisfy the requirements of the Swedish Standards SIS 99 00 - 1867, A-C, Sa 2 1/2.

The material used for sandblasting shall be of such a quality that all impurities can be efficiently eliminated and that its use can be repeated for several times. It means that the grain hardness of materials used for sandblasting shall be 7.5 Mohs.

Washed and dried quartz sand shall be free from dirtiness and impurities, dust and moisture. Granulation of sand shall range within the limits from 0.5 to 1.3 mm.

Grain size of granulated slag from blast furnaces shall range from 0.5 to 2 mm and the slag shall not contain sulfur ingredients, sulfur compounds and other active admixtures.

7.6. Paint Application

7.6.1. General

All paints shall be prepared and applied in accordance with the manufacturer's instructions. Copies of appropriate data sheets and of the relevant parts of this Specification shall be issued to all the supervisors and foremen concerned with surface preparation and coating.  If a manufacturer's instructions conflict with General Technical Specification, a ruling shall be sought from the Engineer.

No thinners or cleaners shall be employed other than those recommended by the paint manufacturer.  Except where otherwise specified or approved by the Engineer all priming paints shall be applied by brush.  Exposure of intermediate coats of paint for periods in excess of a few days shall not be permitted except in the case of work delivered to Site in a primed condition.

The dried films of the specified paints shall be free from bloom, sinkage, sheerness, wrinkling, sagging, curtaining, discoloration and extraneous matter.  No exterior or exposed paintwork shall be carried out under adverse weather conditions.  Painting shall insofar as is practicable be shaded from direct sunlight to prevent wrinkling and blistering.  Whenever possible, exterior painting during the day shall be so programmed as to be carried out in shadow.  Painting of surfaces shall not be carried out when the relative humidity of the atmosphere is such that condensation is present on such surfaces or the application and/or drying of the paints is likely in the opinion of the Engineer to be affected.

The protection of surfaces shall include application of prime coats and protective (covering/finish) coats.  The prime coats shall be applied as described in the leaflets of the manufacturers of corrosion-proof agents.

In addition, the Contractor shall strictly follow manufacturer’s instructions regarding minimum time of curing of fully protected parts of equipment before they are put into operation.

7.6.2. Painting bolted connections

Joint areas for bolted connections shall be masked to maintain the surfaces free from any paint applied prior to making the connection.  Masking shall be removed before erection.

After installation and after all bolts have been tightened, the areas of the connection shall be cleaned to remove all dirt, dust, oil or other contaminants.  Particular care shall be taken to ensure that all traces of oil and grease are removed from bolts, nuts and washers.

Bolts, nuts and washers and any areas exposed at bolted connections shall also be primed as specified, particular care being taken to ensure that any crevices are fully sealed.  The remaining coats of the paint system shall then be applied.

7.6.3. Painting welds

After the completion and grinding of exposed welds, weld spatter, weld residues and all alkaline deposits and contaminants shall be removed from the surface of the steel-work, and welds and any other areas affected or damaged by the welding process shall be blast cleaned.  Primer shall be applied to the blast cleaned areas as specified and the remainder of the paint system applied as necessary to complete the protection across the welded seam and damaged areas to the same state as that existing generally on the faces of the parent metal.  Each coat applied shall overlap the corresponding existing paint coat by 50mm both sides of the weld on each exposed face of the parent metal.

7.7. Epoxy paints

7.7.1. General

In addition to the general requirements of this specification the following conditions shall apply wherever epoxy coating work is being carried out:

- The work shall be to the satisfaction of the Engineer.

- Forced drought ventilation to the approval of the Engineer shall be used wherever required for the needs of personnel or for drying out surfaces.

- Operatives shall work in pairs.

The Contractor shall demonstrate all his methods, equipment and materials before any work commences.  Sample areas of substrate shall be prepared and coated as required by the Engineer and for his approval.

There shall be strict control of surface cleanliness between primer and epoxy coating and between coats of the same.  Vacuum removal of dust and sand shall be employed and contamination shall be removed as specified in appropriate preparation clauses herein.  Where dirt or dust has become trapped in the epoxy coating surface it shall be removed with suitable abrasive paper.  The surface being coated shall be free of visible moisture throughout these operations.

Epoxy coating shall be applied only to clean dry primed or previously coated surfaces.  Any thick runs or collections of paint shall be removed before they harden.  No fewer than two coats shall be applied over the primer by airless spray; no fewer than three by brush.  Each coat shall be distinctly different in color from the primer or previous coat.  The colour of the final coat shall be as required by the Engineer.  Each coat shall be seen to have completely covered the preceding coat without ‘misses’ or pinholes or any areas visibly low in thickness.  A high voltage pinhole detector shall also be used to determine the integrity of the coats.

The manufacturer of the coating shall stipulate primer and epoxy re-coating intervals for all curing temperatures likely to be encountered and these shall be adopted with a maximum tolerance of +4 hours.  Where this is exceeded, the surfaces to be re-coated shall first be suitably abraded or treated with solvent to remove gloss and give key.  Wet thickness gauges shall be used continually by the coating operators to check that sufficient coating is being applied to achieve the desired dry film thickness.

7.7.2. Qualification and Workmanship

All epoxy coating work shall be carried out by a specialist firm or sub-contractor approved by the Engineer.  When applying for such approval, the Contractor shall submit a letter of guarantee from the specialist sub-contractor backed by the paint manufacturer that the product he proposes to supply, when applied in accordance with this Specification and any additional specifications which shall be quoted by the sub-contractor, shall withstand the environmental service conditions to be encountered.  The letter shall quote the guarantee period in years from time of application of the coating, in accordance with the General Guarantee for painting

7.7.3. Material and Equipment

Containers of epoxy paint shall be of a pack-size suitable for complete usage by one operator within the pot life of the material at the highest likely ambient temperature.  The Engineer may approve the supply and use of larger packs but only where the proportioning of the various parts, their mixing, and issue of paint shall be under the direct control of a skilled and experienced operator.  A mechanically operated mixer shall be used and shall be of a design which does not entrain air in the paint.

Except where otherwise specified epoxy resin paints shall be so formulated that the epoxy resin content, together with its curing agent, shall be not less than 40% by weight of the solid binder.  The pot-life of epoxy primers and paints when mixed shall be not less than one hour at the temperature at the place of application at the time of mixing.  When approved by the Engineer shall have regard to the ambient temperatures likely to obtain for field application and may restrict paint application to those times when the temperature is sufficiently low for the specified pot-life to be ensured.

Thinners shall not be mixed with epoxy materials.  Strict control shall be exercised in the issue of thinners for cleaning brushes and equipment.

7.7.4. Fusion bonded epoxy powder coatings

Unless specified otherwise, all steel fabricated pipework and other equipment, where specified, shall have a lining and coating, not less than 250 microns thick, of 100% solids, thermosetting fusion-bonded, dry power epoxy coating.

All traces of grit and dust shall be removed and coating commenced before formation of visible oxidation of the surface.  The metal shall be pre-heated to a temperature recommended by the manufacturer, the epoxy powder applied by immersion in a fluidized bed following which excess powder shall be removed.  The powder shall be allowed to flow out completely before curing.

The thickness of the coating, including any repaired areas, shall be checked with a calibrated tester.  Spark testing, for pinholes, voids, contamination, cracks and damaged areas, shall be carried out using a high voltage spark generator.

Repairs due to coating imperfections or damage shall be undertaken using a brush applied compatible two-pack liquid epoxy compound.  The area to be repaired shall be cleaned to remove dirt, grease, scale and damage coating, which shall be feathered.  Pinhole surface preparation is not required other than removal of detrimental contaminants which impair the adhesion of the repair material.  The surface coating shall be applied by means of an approved applicator.

7.7.5. Steelwork Encased in Concrete

Where a steel member is only partially embedded in concrete, an alkali resistant mastic filled chase shall be provided round the surface junction between steel and concrete.

Sealing and bedding compounds for joints are to be Thiokol polysulfide non-setting Butyl Rubber, or Alkali resistant mastics.

Unless otherwise described in the Contract, surfaces having concrete cast against them, shall be left uncoated and shall be clean and free from loose rust and scale at the time of concreting.

7.7.6. Handling and Storage of Coated Steelwork

The Contractor shall exercise the maximum care in handling and transporting of coated steelwork so that damage to the coatings may at all times be avoided. The use of properly designed slings and soft non-adherent packs is required throughout. All steelwork shall be stored off the ground after preparation for painting, and in conditions free from contamination of any kind and from abrasion or other damage. Polythene wrapped spacers laid between the layers of stacked materials or other approved methods shall be used to prevent damage to the coating. Where cover is provided is shall be ventilated.

7.8. Repairing damaged coats

7.8.1. Defects

Defects are defined in BS 2015 "Glossary of Paint Terms".

The Contractor shall ensure that all coatings are free from defects and adequate in all respects for the purpose intended.

The painting system shall be deemed to have failed if:

(a) After painting, damage has been caused by handling, impact, abrasion or welding;

(b) Any portion of the paint film separates from any other or the parent 	metal;

(c) After painting the total dry film thickness measured by Elcometer is less than that specified.

Failure shall not include:

(a) Loss of gloss;

(b) Variation of shade, not affecting the anti-corrosive properties of the system.

Damaged areas of zinc coatings not individually exceeding 40 mm2 in area shall be made good by the application of a metallic zinc-rich priming paint complying with BS 4652.  Sufficient material shall be applied to provide a zinc coating at least equal in thickness to the original coating.  Factory prepared surfaces, other than zinc coated surfaces, damaged during site fabrication and/or handling shall be treated as described in the following paragraphs.

All slag and spatter shall be removed from areas of welds by chipping hammer and such areas together with all other areas of damaged priming or other damaged coating shall be thoroughly mechanically wire-brushed and given one coating.  The priming coat shall be applied by brush, taking care to cover uneven surfaces completely, particularly those of welds.  Further approved coats shall be applied where necessary to build up the thickness of the repaired coating to at least that of the original coating.  Areas of paint on steelwork which have been damaged shall be cleaned to sound material and the edges of the undamaged paint shall be smoothed with sandpaper to a gentle bevel. The specified paint system shall then be applied to bring the damaged area up to the same state of protection as the surrounding paintwork, with each coat of new paint overlapping the corresponding existing coat of paint by at least 50mm.

Where the steel is exposed, it shall be cleaned to remove all corrosion, by blast cleaning if ordered by the Engineer.  Where epoxy coatings are damaged, suitable repair material supplied by the manufacturer of the original coating shall be applied.

7.8.2. Paint Repairs

Repairing works shall be done in accordance with the procedure proposed for original coating, and with original coats. If original coats for repairing are not available, compatible coats, with quality equal to, or better than the original, may be used. Alternative coats (nature, trademark, color) shall be subject to the Engineer’s prior approval.

Defects such as faulty adhesion, insufficient polymerization, holes, air bubbles, or cracks shall be repaired by removing the faulty paint and re-applying new paint system. Exposed metal shall be prepared for painting according to the aforementioned specifications. When local repair is made, the repair shall encompass an area around the fault area of 5 cm beyond the boundaries each side. The top coat shall cover the roughed old paint surface.

In addition to mentioned above, the Contractor shall repair all damages on anti-corrosion protection layers and painting that may result for improper handling of equipment, or shall inevitably appear during execution the works at the site (cutting and welding the pipes that have been shop protected).

8. Inspection and Testing

8.1. Examination of Welds

8.1.1. General

Welding shall be inspected during and after completion of the work. Quality control of works shall be performed in accordance with QA/QC plan and approved welding procedure.

The Contractor shall notify the Engineer of mandatory hold points beyond which commencing of any work is not permitted. The Contractor shall furnish the Engineer, or full-time weld inspector with reasonable time, facilities and space for inspection, testing and obtaining other relevant information required to check the quality of welding material, and to estimate the progress and condition of the work, and the result obtained.

Inspection or lack of inspection shall not relieve the Contractor of the responsibility for performing welding work in accordance with provisions of this Specification.

All completed welds shall be subject to visual and non-destructive examination to prove conformation to the requirements of this Specification and acceptance criteria of approved standard.  The welds shall be visually examined on the outside surface and, where applicable, in the bore of the pipe by using optical instruments.  The Contractor shall provide photographs of welds, where necessary, to support possible claims.

After visual inspection, the welded joints shall be subjected to non-destructive and hydrostatic pressure testing.

The welds shall be free from defects and shall meet the requirements of a relevant JUS Standard. Any welding work that is not in accordance with the requirements of this specification and approved standard shall be rejected.

All welds found not to satisfy foregoing requirements and/or requirements of approved welding standard shall be deemed to be defective, and shall be repaired by the Contractor on his own expense. Re-welding of joints which do not meet the requirements shall not be performed without the written opinion and/or approval of the Engineer.  Defective welds shall be removed and that section of the joint shall than be re-welded. If weld leaks, it shall not be repaired by mechanical caulking. After the repair is made the joint shall be inspected and checked by repeating the original procedure.

After finishing the welding works, the Contractor shall issue a certificate of conformity stipulating that all works have been made in accordance with the requirements of this specification and provisions of approved standard.

8.1.2. Pipelines / Pipeline Systems (Installations) Weld Joints

Welds inspection and testing refer to all type of the field welds performed during construction of pipelines / pipeline systems (installations), including butt welded joints between the pipes themselves, adjacent pipeline sections, or pipes and fittings, and butt, lap or corner weld joints between pipes and flanges.

Inspection shall include all welding work performed, and equipment and material furnished under the requirements of this Specification. In particular, inspection shall refer to the following:

- preparation of pipe ends

- squareness of ends for welding

- heat protection of anti-corrosion coatings

- alignment of pipe sections to be welded to each other

- checking of clearance between sections to be welded to each other

- welds pre-heating and thermal relieving, where required

- checking of electrodes dryness

- checking of welding apparatus operating parameters, where applicable

- checking of instruments calibration

- weld surfaces finishing, where required

- welds dimensions checking

- visual inspection of finished welds to make sure that the welds are free of unacceptable defects such as cracks

- visual inspection of welds during hydrostatic test to make sure that the welds are free of sweats and leaks

Visual examination of works shall confirm that welds comply with the following requirements:

- profile of external surface

  - weld metal shall be properly fused with the base metal without significant undercutting or overlapping at the toes of the weld

  - the toes of undressed welds shall blend smoothly and gradually into the base metal

  - undercutting and overlapping at the undressed weld toes shall be permitted providing that either or both do not exceed a total of 25mm in any 100mm length of weld; undercutting, irrespective of length, shall not exceed a depth of 20% of the nominal pipe thickness or 2 mm, whichever is the smaller

  - external reinforcement of undressed weld shall be allowed to be between 1.5mm and 5mm high measured from the outer surface of the base metal; this reinforcement shall be symmetrical to the centreline of the joint and shall be of smooth contour

  - the toes of dressed welds shall be free from undercuts

  - the surface of the welds shall be free from porosity, cavities and loose scale

  - the stop and start of each pass of weld shall merge smoothly and shall show no pronounced hump or crater in the weld surface

- profile of internal surface

- weld metal shall fuse the base metal at the root without protruding excessively into the bore; the maximal penetration in bore and maximal restriction in bore diameter shall be as per BS 2971, Section 8

- root concavity at the bore shall be acceptable providing that there is complete root fusion and that the thickness of the weld is not less than the pipe thickness

Weld testing activities shall include non-destructive examination of all field welds and hydrostatic testing to proof structural integrity of the pipelines materials and welds.

The field weld joints shall be subject to 100% non-destructive testing, specifically using a combination of ultrasonic and radiographic examination.  The ultrasonic method shall be used along the entire length of the sieve, while radiographic method shall be used along the length of the sieve where the defects are detected and at least at 10% of length of welded connections, including all points of cross welding.  Additionally, if defects are noted, the Contractor shall inspect the sieve over the entire length via visual, “outside” control, before and during welding (using penetrating or magnetoscopic method), and after welding, using “inside” control, over the length of the sieve (max 50%), according to the instructions given by the Engineer.  In case of defects, further, the inspection shall cover the entire length of the sieve.

When using radiographic or ultrasonic examination for assessment the welds, revelation of improper joint set-up, irrespective of weld quality, could of itself be cause for rejection.  If welding quality falls, the level of radiographic testing shall be increased to 100%, until welding quality is restored.  When random radiographic or ultrasonic examination reveals unacceptable defects in a weld, at least two further welds in the group represented by this weld shall be examined by the same method.

If the examination of these further welds in the group reveals no unacceptable defects, the defect in the first weld shall be repaired and re-examined by the original method. If the repair is satisfactory, the group of welds shall be accepted.

If the examination of either of the further welds in the group reveals unacceptable defects, each weld in the group shall be examined by the same method. Unacceptable defect shall be repaired and then re-examined by the original method.

Depending on the method of non-destructive examination applied, the weld external finish and/or surfaces adjacent to the weld shall be in accordance with the finish number as it is defined in approved welding standard.

All butt weld joints made in road, rail and watercourse crossing shall be subject to radiographic examination.  All tie-in butt weld joints made following hydrostatic test of sections shall be subject to radiographic examination supplemented by ultrasonic testing.  Any field weld which fails a pressure test shall be repaired and subjected to both radiographic/magnetic particles and ultrasonic inspection.

8.2. Hydrostatic Pressure and Leakage Testing

8.2.1. General

The Contractor shall conduct the hydrostatic pressure and leakage testing of all pipelines that belong to the scope of the Works. That shall include test planning, performance and interpretation of test records. The purpose of these activities is to demonstrate the integrity of the constructed pipelines and provide precise and complete test data that shall allow an effective assess of the tests validity, i.e., the quality of the works performed. The term „integrity of the constructed pipelines“ refers to pipe strength proof, leak in  the welded joins, leak in the mechanical joints and leak on the valves and associates.

This section specifies criteria for test pressure limitations and durations, sitting of test sections and tests acceptance criteria. In addition this section provides a general methodology for tests implementation. However, concerning this general methodology, the Contractor shall prepare a detailed, step-by-step procedure which shall be an integral part of his Methods Statement.

The Contractor may propose an alternative test methodology, which for the Engineer’s approval must be obtained.  The testing method shall refer to recognized codes and standards.

The testing procedure shall develop the following steps necessary to complete testing requirements:

a.	test planning

b.	test performing

c.	post test analysis

The test planning shall include the following considerations and test preparation activities:

•	test pressure

•	duration of test

•	test medium

•	test sections (pre-testing, aerial cross testing)

•	internal cleaning and inspection

•	pre-test calculations

•	test equipment and instrumentation

•	test sensitivity and accuracy

•	establishing pass/fall criteria – acceptance criteria

During performing the test, the following shall be observed, considered or undertaken:

•	line-fill, pressurization and stabilization

•	monitoring of ambient conditions

•	recording the pressure

•	recording the temperature

•	entrained air

•	inspection

•	injection

•	bleeding

•	interim calculations

•	depressurization

•	dewatering and disposal of test water

Post-test analysis shall include the following:

•	evaluation of test data

•	acceptance criteria

•	contingency plan in even of leak or rupture (if any)

•	certification of conformity

8.2.2. Test Planning

The Contractor shall determine the minimum and maximum test pressure ranges for each pipeline, or section of pipeline, which shall be subjected to the hydrostatic test. The test pressure ranges shall be determined on the basis of the maximum operating pressure, pipe dimensions and mechanical characteristics, and pipeline route profile as they shall be outlined in the Detailed Design.

The hydrostatic test pressure in any part of the system under test shall not be less than the lower of:

•	150% of maximum operating pressure, or

•	the pressure that induces a hoop stress of 90% of the specified minimum yield stress of the pipeline material in the system under test.

The pressure at the point of application shall be such that the test pressure is achieved at the highest point in the section under test. The additional static head at any point in the section shall not cause a hoop stress in excess of specified minimum yield stress of the pipeline material.

The hydrostatic test shall be performed under stabilized conditions and held for a minimum period of 24 hours.

As an alternative to the procedure described above, a cyclic testing procedure may be allowed.

Pneumatic testing shall only be carried out when hydrostatic testing is not convenient, as it may be concerned for pipelines set down to the bottom of the sedimentation pond. The pneumatic test pressure shall not be less than 125% of the maximum operating pressure. The pipelines subjected to the pneumatic test shall be pre-tested at the pressure of 1.5 bar before commencing the full test. The strength test held for the period of ½ hour shall be followed by the leakage test at the pressure not less that 110% of the maximum operating pressure. The leakage test shall be held for a period of 24 hours. The pneumatic tested pipelines shall subsequently be tested with water after installation, in a period of time not less than 4 hours. The pneumatic testing must be conducted with extra safety precautions to protect person from injury.

Pressure relief devices, if provided with the tested pipeline, must be identified and recorded. If necessary, such devices shall be removed or isolated during performing the pressure test.

It is recommended that the pressure testing be conducted with water which shall be clean and free form any suspended or dissolved substance which could be harmful to the pipe material or internal coating, or which could form deposits within the pipeline.

In the testing plan the Contractor shall identify, for each pipeline, the sources and quality of media he is intending to use for the purpose of testing.

The Contractor shall prepare a description of the pipeline section to be tested. He shall prepare a scheme showing the pipeline section with accurate total length and lengths of internal and external sections (if any), pipe elevation, location of valves and fittings, pipe material, diameters and wall thickness.

The length of test sections shall be governed by the following:

•	maximum and minimum test pressures

•	proximity of water sources, available rate of withdrawal and disposal 	requirements

•	location of sectional valves that make a natural division in the pipelines

•	environmental constrains; source of water and receiving environments

During testing external pipeline (pipeline buried in the soil), field welds shall be accessible to enable assessment of weld joints integrity. It is recommended that the test is conducted against blind flanges, pan blinds, gas bags or in-line test tools. In-line valves shall not be used for pipeline sectioning. If testing against blinds is not quite practicable, the Contractor may consider the testing against closed valves. Such testing must in advance be approved by the Engineer.

Prior to hydrostatic testing the pipelines shall be subject to visual inspection and internal cleaning.

If testing with water, the Contractor shall prepare a line fill plan to make testing section free from the air. For this purpose the installed high point vent valves shall be used. The filling velocity shall not exceed 0.3 m/s. Otherwise, the Contractor shall consider other means as pigging, water flushing at a fast enough, but appropriate rate, or installing temporary vent cocks.

Before commencing the test, the Contractor shall perform a pre-test calculation to obtain a theoretical value of the DV/DP (the change in volume for an associated change in pressure of a known volume under pressure). This information shall be used to determine whether entrained air exists in the pipeline under test and to establish acceptable differences between the theoretical and field values of DV/DP. If a volume of air content exceeds 1% of volume of the tested section, or linear slopes of the theoretical and field volume/pressure ratios differ by more than 10%, the test section shall be bled of the air at a high point, or the line shall be refilled.

The Contractor shall prepare and submit to the Engineer for approval a scheme of testing block/manifold, detail drawings of injection, bleed-off and test manifold points, as well as a list of testing equipment and instruments with their basic technical characteristics. The list of testing equipment shall comprise pumping or compressor assembly for filling the pipeline and/or maintaining the pressure during testing, tools for inspection of interior of the pipelines and detection of leakages. All testing instruments must be calibrated immediately before commencing the test. Certified calibration reports shall be submitted to the Engineer on his request.

The Contractor shall be aware of the following factors that affect the accuracy of test results:

•	fluid temperature

•	entrained air

•	coefficient of test medium thermal expansion

•	accuracy of the instrumentation

Fluid temperature is affected by a variety of factors and hence may change during testing. Pressure data that does not correspond correctly to temperature changes may indicate a leak or poor placement of the temperature recording instruments.

Entrained air may prevent stabilization of the testing media during a test or may prevent the detection of a leak. Due to air compression and expansion characteristics, the presence of significant amount of entrained air shall slow down pressurization of the pipeline section and hide the small leak.

Special attention to fluid temperature must be paid when the pneumatic test is going to be performed. High coefficient of thermal expansion makes the air sensitive to changes of temperature. Therefore, for the same temperature recording accuracy, a ratio of volume/ pressure to temperature changes may be higher when compare with water as a test medium.

The recommended accuracy of the instrumentation to be used in the test shall be as follows:

- pressure recording devices, including deadweight tester, shall have an accuracy of ± 0.07 bar; for a documentation purposes, an electronic pressure recorders with high resolution shall be provided to enable collection of more frequent and accurate data

- temperature recording devices shall have a high accuracy; the output resolution for a water pressure test shall be 0.06ºC, or  a few times higher for a gas test; it is recommended that recorders have a digital readout and to include options for direct printing or outputs that can be stored and printed later on

- fluid volumes to be injected or bled during testing shall be measured using the standard measuring cup (container) with the most precise graduations available

8.2.3. Performing Test

Before applying pressure, all components in the test section must be inspected to check the following:

- all components of the test section are restrained

- mechanical connections are tightened per manufacturer’s instructions

- if backfill provides restraint, it is properly placed and compacted, but joints and connections are exposed for inspection

- end closures are pressure-rated for test pressure

- make sure that restrain forces shall not apply to the structure that are not designed for such purposes

To prevent influence of ambient conditions on the accuracy of hydrostatic test results, the following shall be taken into consideration before commencing the test:

- test shall not be conducted in rainy or wet conditions since visual leak detection may not be possible

- to reduce the amount of bleeding that may be required for the pipelines exposed to sun, aboveground pipe tests shall be conducted on cloudy and cool days to minimize the thermal heating of the pipes

Pressure recording equipment shall be installed so that localized surges from the test pump or bleed lines do not interfere with the readings.

Ambient temperature shall be taken with a digital thermometer throughout the test. Where a significant difference in pipe or fluid temperature can be expected, multiple recorders shall be used. This shall be applied to the sections with:

- significant portions  of aboveground  and belowground pipe

- pipe segments exposed to the sun and shade

- aboveground (exposed) pipe that has significant variations in pipe diameters

Medium test temperature shall be measured directly by using thermo wells or by drawing-off a small quantity of tests fluid and immediately measuring its temperature (only when the ambient temperature is within 7ºC of the test medium temperature, and the temperature recorders have a quick response time). The temperature recorders must not be exposed to direct sun and wind that may have influence on measuring accuracy.

In order to enable thermal stabilization, an equalization period of time shall be allowed. The settlement time shall be determined concerning ambient temperature, temperature of filling medium and the diameter of the pipeline being tested.

During initial pressurization a field values of DV/DP shall be obtained and than compared to the theoretical values. A field value of DV/DP that is smaller than the theoretical DV/DP indicates incorrect measurements. A field value of DV/DP that is greater than the theoretical DV/DP indicates presence of air that must be bled at a high point of the section. When obtain field DVD/DP range that corresponds to a volume of air that is 1% or less by volume of the test section, gradual pressurization could be continued until reaching maximum test pressure. During pressurization, valves, flanges and other appurtenances shall be checked for leaks. If leaks occur, the Contractor shall repair the malfunctions before proceeding to the final testing.

During the test, the following data shall be obtained:

•	deadweight/pressure readings

•	temperature reading(s) of the test medium

•	ambient temperature reading, measured in shade

•	volume bleed or lost through leaks

•	volume injected

Test data shall be read and recorded in 15 minute time increments, as a minimum, or test data shall be continuously taken if digital instruments are provided.

Valves, flanged and threaded joints, and accessible welds shall be visually inspected in appropriate intervals of time after commencing the test. Visual inspection results and repairs on any leakages shall be documented.

Provisions for measuring the volume of fluid injected into the test section shall provide an accurate measuring of the volume. This could be obtained by injected fluid from graduated container, by metering or by counting the number of piston pump strokes. As a check, a pressure reading before and after injection shall be taken, and the pressure difference multiplied by the field DV/DP to obtain a calculated injection volume. Actual injection volume, calculated injection volume and field DV/DP shall be documented each time when it is measured.

Fluid bled that may be required to prevent pressure of exceeding the maximum test value, shall be measured with an appropriate type and size container showing accurate graduations. A volume of bled fluid shall be documented.

A final field DV/DP value shall be taken prior to depressurization. Depressurization shall be gradual. Depending on quality of testing fluid and water pipeline purpose, filling water may be bled, or used to fill another section, or may be left in the section if so approved by the Engineer. The gas pipelines shall be dried after completion of testing.

8.2.4. Post Test Analysis

Evaluation of test data shall include post-test calculations to correlate pressure, temperature and fluid volume bled or injected. If multiple temperature probes are used to collect data, a weighted average temperature based on the volume shall be used to calculate the changes in volume.

The test shall be considered to pass successfully if there is no leak in a tested continuously welded steel pipeline. An acceptable volume change is allowed regarding only the accuracy of measuring instrumentation. If testing of a pipeline section is conducted against low-leakage section valves, the rate of a valve allowable leakage shall be taken into consideration when evaluate the testing data.

Pneumatic leak testing of completed service air pipeline installation shall be considered to pass successfully if leaks don’t exceed 3% of designed maximum consumption in the system.

Any work that is not in accordance with the approved method of testing, or does not conform to the applicable provisions of this Specification, shall be rejected.

If pressure reading indicate that a leak exists in a section of pipeline being tested, steps shall be taken to locate and repair, or replaced damaged pipe and restart the test. The procedure for locating a leak shall include the following steps (as applicable):

- visual examination of the line to check for signs of water leakage

- use a sonic leak detector

- close any mainline valves located in a test section to isolate the leak in a shorter section

- de-water, segment in shorter test section (if applicable), refill and pressurize the test section to isolate the leak in a shorter section

Before pressurizing the test section again, a period of time shall be reserved to allow for venting and repairs to be made.

After pressure test of a pipeline is successfully conducted, the Contractor shall provide the Engineer with a test report that shall include all relevant testing data (sketches and descriptions of tested section, equipment and instrumentation, nature and quality of testing fluid, all recorded data, pre-test, test and post-test calculation, visual inspection documentation). The reports shall be signed by all relevant persons who have been participated in the testing. In addition to the reports, the Contractor shall provide the Engineer with a certificate conforming that the test is conducted in accordance with the approved testing procedure and applicable provisions of this Specification.

8.3. Valve Verification Prior to Start-up

Before putting the manually operated valve into service, the following shall be verified:

- the external stem thread, the rolling bearings, and gear units are properly lubricated (where applicable)

- reliable and correct actuation of the valve; verification shall be done by repeatedly opening and closing the valve to the respective limit positions, and by visual inspection ( before the valve is connected to the moving mating flange, e.g. dismantling joint or compensators)

- make sure that direction of actuation is correct

- check existence and proper function of mechanical end stops, locking devices, and position indicators

For electrically, pneumatically and/or solenoid operated valves, additional verifications shall be done in an appropriate order of sequence:

- the electrical connections  are correctly wired

- the electrical data such as voltage, current, frequencies, etc. agree with the data for the mains connection provided on the site

- the pneumatic hoses are properly fitted to the actuators

- the limit and torque switches, and position indicators or monitoring devices respond in accordance with manufacturer’s data

When valve electric actuator is not equipped with de-clutchable manual drive, manual override operation shall also be checked, as in the following steps:

- ensure that electrical power to the unit is off

- remove the valve position indicator pointer

- using a wrench of appropriate size, push down on indicator shaft to disengage it from output gear, and then turn the shaft to required position

- use Open and Close lettering and a direction of travel arrow molded into the housing for easy reference and position indication; observe the mark on the indication shaft which is in alignment with the valve disc position

- return to electrical operation by turning the power on to the unit; the shafts shall re-engage the output gear when electrical power is applied to the actuator

- replace the valve position indicator pointer

If for any reasons, the installed valve has to be repaired, and/or dismantled and re-installed, the following must be taken into consideration in addition to the manufacturer’s instructions:

- before commencing any work on the valve, make sure that the valve and the adjacent equipment are pressure-less and properly drained

- if necessary, the valve shall be flushed with clean water, and properly cleaned

- during repair work, the valve/system must be secured against unauthorized start-up

- when the valve is removed from the pipeline, use the procedure opposite to the installation procedure

- only original spare parts shall be used

- use new sealing elements and packing rings whenever the valve is reassembled

- make sure to reassemble all dismantled components in their original installation positions

- if actuators powered by an external source of energy need to be removed from the valves, the energy supply must be shut-down and secured against unauthorized re-starting prior to commence any repair works

- electrical connections must be dead and isolated from the power supply

- pneumatic components must be isolated from the air supply lines, and depressurized

- after repair works on the valve and/or its externally energized actuator, the limit and torque switches, as well as position indicators or position monitoring devices, shall be checked to respond, and set again if necessary

8.4. Inspection and Testing of Paints and Protective Coatings

8.4.1. References

While carrying out the inspection, the reference shall be made to:

- These Technical Requirements;

- Regulations for technical steps and conditions for corrosion protection of steel structures – Official Gazette No. 32/70;

- JUS Standard C.T7.120/71 – metal coatings of tin aluminum and lead, applied by method of metal spraying;

- JUS Standard H.C.8.-50/68 – inspection methods for checking coating materials for railway vehicles and steel structures.

8.4.2. Instruments and Apparatus for Inspection of Works

- Swedish Scale for inspecting the degree of cleanliness of the surfaces after sandblasting;

- Apparatus for measurement of the wet film coat thickness – ERICHSEN – Type 234/IV, according to ASTM D-1212-54, or similar

- Apparatus for measurement of dried film coat thickness – Elcometer, Micro test, ERICHSEN, and similar;

- L.V. defect scope for measurement of dry film porosity;

- Apparatus for measurement of adhesion of cured film to the metallic base – ERICHSEN – Type 295/II and Type 295/III, or similar, according to DIN 53151;

- Contact thermometer for measurement of temperature of steel structure surfaces to be protected;

- Hygrometer with thermometer for measurement of relative humidity and temperature of ambient air.

- Apparatus for measuring the electric permeability of outside anticorrosion protection.

8.4.3. Testing

The following tests shall be carried out:

(a)	Checking wet film thickness

Wet film thickness gauges of an approved type shall be provided for 	each painter to check the rate of paint application.

(b)	Checking dry film thickness

The thickness of the built-up dry film after each paint coat applied to 	steel or other magnetic surfaces shall be measured systematically, with 	a dry film thickness gauge.

(c)	Holiday detection on steel and iron surfaces

The Contractor shall use a suitable method of detecting pinholes in the coating system after trials on test plates.  The sweep voltage on high voltage dc equipment shall not exceed half the voltage required to spark through the complete paint system specified.

8.4.4. Inspection Books

The inspection books i.e. records shall be kept both during storing of paints and during execution of the work on protection against corrosion. The inspection books shall contain all the data on the conditions under which the material was stored and the work executed, entering into books the results of input, interim and the final inspection as well. These books shall be kept by the supervising service staff of the Contractor responsible for the workshop protection against corrosion. The books on the finished site protection work shall be kept by the Engineer.

8.4.5. Input Control

Agents for coating of equipment procured by the Contractor responsible for protection against corrosion shall be checked in the following way:

- The Contractor shall furnish to the Engineer the paint manufacturer certificate for every lot of the paint supplied.

- The Engineer shall check whether the paint is supplied  in the original packing and whether it is marked as specified.

- The Contractor shall furnish one copy of the certificate on quality testing to the Engineer.

- The permissible deviation from the factory certificate for the basic components of the supplied paints shall be within the limits ± 3 %.

- The Engineer shall make sure that the life of the coating agents has not expired and shall inspect the correct storing thereof.

8.4.6. Interim Inspection

The interim inspection shall be carried out for every operation separately. All the phases of work shall be executed in accordance with the conditions and procedures as specified herein.

Inspection of the protected surfaces shall be made regularly after completion of each phase of work.

Checking of working conditions such as temperature, relative humidity, protection against sun and against other atmospheric influences, shall be made during execution of the work and the records thereon shall be duly kept.

It is particularly important to investigate all equipment after transportation and handling during installation; all the defective coatings of protection that are found shall be properly remedied.

8.4.7. Final Inspection

The final inspection shall include checking of the total thickness of the coatings. The maximum permissible deviation shall be ± 7 %.

The measurements to be made are as follows:

- the porosity of cured coating film. No porosity shall be permitted.

- adhesion of the cured coating film; the maximum permissible failure on 100 pieces, 2 x 22 mm squares shall be 5%, and if larger peelings are noticed, the protection coating shall be reapplied (DIN 53151).

- the coating evenness.

- the total thickness of cured coating film.

If the film is found to be porous, another protection (covering) coating shall be applied and the porosity checked once again.

8.5. Tests during the Works, on and after completion

The purpose of the test activities is to prepare and check the start-up through and complete to avoid malfunction, damage to equipment, or future operating problems that might result of installation errors or errors in starting procedures. All tests are going to be executed as described in STS, Chapter 4. “Tests”

The Contractor shall prepare a start-up check list for each installation and organize start-up team with the following suggested personnel:

•	start-up coordinator – an operation specialist provided by the Contractor

•	mechanical contractor - provided by the Contractor

•	electrical contractor - provided by the Contractor

•	instrumentation contractor - provided by the Contractor

•	operators - provided by the Contractor/Employer

Representatives of the Employer, Engineer and Supplier shall participate in all phases of all tests.

The duty of the start-up coordinator is to implement the testing plan devised by the Contractor (Test during the works) or the Employer/Supplier (Tests on and after completion). During all phases of start-up activities, the start-up members provide both expertise in their respective fields and verification checks. After start-up, the team shall remain at the site to facilitate fine adjustment and debugging.

The start-up check list must be specific for each installation and shall contain pre-visit check and pre-start-up check items. The list of items attached hereinafter is a proposal and shall be supplemented with operating and maintenance manuals and troubleshooting and remedy measures charts supplied by the Supplier.

Before visiting any installation, the start-up team shall review all relevant documentation, such as the Detail Design, Specification, control section of O&M manuals and other documents that may be adaptable to start-up.

C. 	ELECTRICAL DESIGN

I. DESCRIPTION

# 1.1	Basic information

The potable water treatment plant PWTP Majdevo, capacity 700 l/s, and 20km long water mains from village Majdevo to the town of Kruševac were built between 1979 and 1984. WTP Majdevo treats raw water from the artificial lake Ćelije.

Nowadays, this facility supplies potable water to complete town area and the majority of rural areas within municipality of Kruševac. The supply network is over 450km long and reaches to 140,000 inhabitants (i.e. more than 30,000 water connections). Besides the municipality of Kruševac, potable water from the system is already supplied to municipality of Aleksandrovac. With all the design activities already completed and plans set for inclusion of municipalities of Ćićevac and Varvarin into the regional water supply system Ćelije, the expansion of the system is soon to be expected.

The plans also incorporate WTP Majdevo capacity expansion up to 1180l/s, supply network expansion for additional 1200 connections and completion of hydraulic mains circumferencing the town of Kruševac.

At the moment, construction of water pipelines to Ćićevac, Stalać and Varvarin enters its final stage. Meanwhile, water from the system is already supplied to the settlements on the eastern edge of the municipality of Trstenik. According to the plans, several rural areas from municipalities of Paraćin and Ćuprija will also be incorporated in the system, which will eventually become truly regional water supply system. Expected increase in number of customers will inevitably bring changes to modalities of system everyday operation.

The system control and maintenance difficulties were already present in such a wide area system, even before the recent plans for its expansion, mostly due to absence of a centralised site from which all relevant system parameters could be monitored. Therefore, public communal company JKP "Vodovod" Kruševac established the first centralised control and monitoring system (CCMS) in 1995 using modem communications, covering Ćelije dam reservoir, WTP Majdevo and main town drinkable water storage reservoir Bagdala. This system is still functional. The CCMS system was renewed in 2004 and, in addition, pumping station PS Bagdala and storage reservoir Šumice were integrated, as well as the first local command centre Bagdala. Shortly after that, local CCMS centre Ćelije was modernised, while the metering and regulation station Lipovac was completely outfitted with control and monitoring equipment. During 2007 and 2008 a series of pumping stations and reservoirs were adapted and integrated into the existing CCMS.

As a part of CCMS modernisation, the main command and control centre (CCC) Direkcija was established within the management building of JKP Kruševac. According to the plans, this main CCC will be moved on the location of Lipovac, where JKP Kruševac has its main maintenance facilities. Modernisation also included installation of radio base station and registration of the used radio frequencies with the Serbian Republic Telecommunication Agency RATEL. The main server computer was installed within a LAN, with properly configured SCADA software. Further expansions of the CCMS should primarily include remote locations of regional part of the water supply system, especially because of their significance and the fact that corresponding blueprints did not consider at all the aspects of centralised monitoring and control.

Having in mind current state of the regional water supply system Ćelije and all the plans for its further expansion, establishing of an all-inclusive CCMS becomes a necessity. The general design, which is ground for this tender documentation, covers all technical elements crucial for centralised control and monitoring of the regional water supply system Ćelije. Apart from control and monitoring of regional part of the system, this design also covers all the elements of municipality water supply system of the town of Kruševac, which covers the town centre and the most of rural areas of the municipality as well.

# 1.2	Technical design

## 1.2.1	Introduction

General design of the CCMS of the regional water supply system Ćelije was proposed in accordance with the good engineering practice and the main objective of the system - to provide continuous technical surveillance and full resources control of the regional water supply system. The main criteria underneath the design were:

- The reliability of monitoring and control functions of the CCMS,

- The new CCMS must be based on the existing CCMS,

- The possibility of multi-stage CCMS realization,

- Taking into consideration development plans for the regional water supply system.

Reliability criteria mainly impose the choice of measuring, controller, communication and networking equipment, as well as the monitoring and control functions of various computers within the CCMS. Reliability is further improved by taking into account experiences with similar CCMSs in other municipalities in Serbia.

To make the future CCMS feasible at all, the design had to take into account the state of the existing technological equipment, especially electrical and measuring equipment. The existing functional CCMS was particularly considered, since at the moment it encompasses four command and control centres and a series of remote locations. Therefore, the existing CCMS must be preserved and fully incorporated into the future CCMS, its present functionality completely retained.

This document deals exclusively with works and locations foreseen for the first stage of the project realization, out of the three stages for the complete CCMS. The third and the last stage of realization will eventually include the objects that are being designed right now.

### 1.2.1.1	Specific equipment choice demands

Since the future CCMS must be fully compatible with the existing CCMS, the two types of equipment must be specifically chosen in advance: controller and radio-communication equipment. The general design, which is the base for this document, predicted the use of the same types of the control and radio-communication equipment in the new CCMS as those already used in the existing CCMS. The significance that these two types of equipment generally have in CCMSs brought to such a decision.

The existing CCMS already has programmable logic controllers (PLCs) of only one manufacturer, "Omron", all of type CJ1M, and hence the same type of PLC is foreseen in the new CCMS. Criteria used in general design for such a choice were:

- Technical characteristic of aforementioned PLC type can completely satisfy needs of the new CCMS, as well as subsequent improvements that can be forecasted at the moment (e.g. optimised algorithms for energy saving, loss reduction etc.)

- The ratio of number of already installed PLCs and total number of PLCs in the new CCMS is in favour of the choice of the same type of PLCs. Possible replacement of existing PLCs with the equipment of other type/manufacturer, due to equipment unification, would be economically and technically unjustified.

- Unification of all of the PLCs is also in favour of designer's decision. It simplifies maintenance, reduces its costs, as well as the costs for the maintenance staff training.

- The qualifications and experience that the maintenance staff has already got for existing PLCs, are also in favour of designer's choice. Additionally, the structure of the maintenance department doesn't allow simple adoption of maintenance procedures for high-tech PLC equipment, neither is likely that structure will change in close future due to heterogeneous electro-mechanical equipment that maintenance stuff already has to cope with. Therefore, introduction of PLCs of another type/manufacturer could severely impede the maintenance of future CCMS and probably lead to its partial or total failure in a shot time period.

- Existing manufacturer support for the specific type of PLC can guarantee availability of spare parts and technical support during considered time period.

Radio-modems and a base station of type T96SR, manufacturer Dataradio, accompanied by appropriate antenna systems, protective and diagnostic devices provide radio-communication within the existing CCMS. Just as in the case of PLC equipment, the general design adopted the same type of radio-communication devices for the new CCMS. This particular choice is justified by the following:

- Technical characteristics of chosen radio-modems completely satisfy the existing CCMS, as well as the newly designed CCMS for the predicted system lifetime.

- There are very positive experiences with the same type of the devices, gained from other water supply systems in Serbia, especially considering reliability.

- Number of already installed radio-communication devices undoubtedly gives designer's choice significant advantage. Especially with this kind of equipment, introducing another type of radio-modems would very likely create compatibility problems with existing radio equipment and that would effectively shut down the existing CCMS. In that case, replacing the existing radio-modems with a new ones would be inevitable, possibly including other auxiliary radio-equipment (antennas, protective or power supply devices) or even PLC's communication hardware/software for radio-modem support.

- Unification of radio-equipment will consequently simplify maintenance. This also is in favour of designer's choice.

- Maintenance staff has been already trained to do basic maintenance and primary diagnostics, and that fact also supports the choice.

- Existing manufacturer support for the specific type of radio-modems can guarantee availability of spare parts and technical support during considered time period.

## 1.2.2	Description of the regional water supply system Ćelije

- At this first stage of the CCMS realisation, total of 34 locations of the regional water supply system will be included, some of them already integrated into the existing CCMS. The objects at these locations are categorised according to their primary purpose:

|  | - Object category | - Acronym |
| --- | --- | --- |
|  | Command and Control Centre | CCC |
|  | - Distribution Network | - DN |
|  | - Metering and Regulation Station | - MRS |
|  | - Storage Reservoir | - R |
|  | - Pumping Station | - PS |
|  | - Pumping Station and Reservoir | - PSR |
|  | - Hydro Press (Hydro Booster) Station | - HP |
|  | - Hydro Press Station and Reservoir | - HPR |
|  | - Chlorination Station | - HS |

- For the simplicity of monitoring and control within the future CCMS, all the locations and objects were clustered into six groups, called subsystems:

- The Regional System,

- The II Supply Zone System,

- The System East,

- The Rasina Wally System,

- The System West - Župa,

- The Morava System.

- Within each of these subsystems (except for the Regional System), locations are further classified into distribution networks, this time dominantly by criteria of technological interconnection. The first stage of the CCMS realisation include all the locations belonging to the Regional System and only some objects from three another subsystems. The list of subsystems and belonging locations for the first stage of CCMS integration is shown bellow:

| - 1. | - Subsystem "The Regional System" |  |
| --- | --- | --- |
|  | - Command and Control Centres | - CCC1 Lipovac - CCC2 Direkcija - CCC3 Majdevo - CCC4 Bagdala - CCC5 Ćelije |
|  | - Metering and Regulation Stations | - MRS Lipovac - MRS Kruševac (Makrešane) - MRS Stalać - MRS Varvarin - MRS Ćićevac |
|  | - Storage Reservoirs | - R Lipovac - R Bagdala - R Todorova kula (Stalać) - R Varvarin - R Ćićevac |
|  | - Chlorination Stations | - HS Lipovac |
| - 2. | - Subsystem " The System East" |  |
|  | - Distribution Network DN Gaglovo 2 | - PS Gaglovo 2 - HPR Mali Šiljegovac |
| - 3. | - Subsystem " The Rasina Wally System" |  |
|  | - Distribution Network DN Naupare | - PS Naupare 1 - R Naupare 1 - PS Naupare 2 - R Naupare 2 |
|  | - Distribution Network DN Šogolj-Meševo | - PS Šogolj - R Meševo 1 - R Meševo 2 - HP Cerova |
| - 4. | - Subsystem " The Morava System" |  |
|  | - Distribution Network DN Srnje (Krvavica, Padez) | - PS Srnje 1 - PSR Srnje 1 (Krvavica and Padež) - R Krvavica - R Padež - PS Globare - R Globare - PS Srnje 2 - R Srnje 2 |

- Although all of command and control centres formally belong to subsystem "Regional System", these centres will provide control and monitoring functions for the entire water supply system in final stages of its realisation, not only for the "Regional System". However, functions of particular centres will differ, according to organisational needs of JKP. The following command and control centres are anticipated for the regional water supply system:

- The command and control centre CCC1 Lipovac, located in the main maintenance facility of JKP company, in village Lipovac, 6km south from the town centre, intended for the main CCC from where the entire regional water supply system would be controlled and monitored. This centre will be the main operational centre and will coordinate with the maintenance department within JKP. The centre does not exist yet.

- The command and control centre CCC2 Direkcija, located in the main management building of JKP (Direkcija) and it is intended for supervisory monitoring of the entire regional water supply system. It will also serve as an alternative centre for the operational control and as development centre. This CCC already exists within the present CCMS as the main command and control centre.

- The existing command and control centre CCC3 Majdevo is situated within WTP Majdevo, some 20km south from town centre, mainly for control and monitoring purposes over the water treatment plant. Although water treatment process is not subject of this project, certain monitoring functions over the basic water treatment parameters will be integrated into the new CCMS. In the later stages of the CCMS integration, the CCC3 Majdevo will gain full control over three distribution networks (DN Majdevo, DN Aleksandrovac and DN Nabrđe) within subsystem "The Rasina Wally System".

- The command and control centre CCC4 Bagdala is placed in the vicinity of the main town storage reservoir R Bagdala, at the top of the hill Bagdala. This CCC is already operating in the existing CCMS as an auxiliary centre for control of distribution network DN Šumice, within the subsystem "The II Supply Zone System". The CCC4 Bagdala will retain its present functionality in the new CCMS, after necessary adaptations.

- The present command and control centre CCC5 Ćelije is within the main management building of dam and reservoir Ćelije, nearly 25km from the town centre up the Rasina river. This CCC is already operating as the main control and monitoring centre for the dam and the reservoir (artificial lake). At this stage of the new CCMS realisation, only monitoring functions will be integrated into the system, whilst the CCC5 Ćelije will be provided exclusively with the basic information concerning the regional water supply system. This CCC will not have any command functions within the new CCMS.

- Command and control centres' functions are defined to meet organisational needs of the public communal company and to reflect technological requirements. Command capabilities of the centres are summarised in the following table:

| - CCC | - Issuing commands |
| --- | --- |
| - CCC1 Lipovac | - To all locations |
| - CCC2 Direkcija | - To all locations |
| - CCC3 Majdevo | - Locations within DN Majdevo, DN Aleksandrovac, DN Nabrđe |
| - CCC4 Bagdala | - Locations within DN Šumice |
| - CCC5 Ćelije | - None of the locations |

- Detailed descriptions of present state for each of the centres, required communicational and technological interconnections between them and anticipated works in order to integrate them into the new CCMS, can be found in a separate section of this documentation.

## 1.2.3	The CCMS configuration

- The centralised control and monitoring system in public communal company JKP Vodovod-Kruševac is built on PLCs networks interconnected with server and PC station networks. Network design reflects the CCMS requirements.

- PLCs are given the role of main acquisition and control devices and hence they are directly attached to sensors, indicators and actuators. They are located in all the objects of the regional water supply system, in the vicinity of technological equipment attached. On the other hand, monitoring PC stations have a primary role of HMI devices, and are not physically connected to technological hardware. These stations are located in command and control centres. In order to link these two aforementioned types of computers, there are special additional PLCs and servers, all bind in computer networks of appropriate topology and communication technology.

- The network used for interconnection of PLCs is based on radio and wireless Ethernet technology. An Ethernet network, with both wired and wireless segments, connects monitoring stations and the server.

### 1.2.3.1	A survey of networks used

- Having in mind the existing functional CCMS, the following computer networks are designed for the new CCMS:

- Four independent networks based on radio-modem communication, using separate simplex frequencies within the band that corresponds to wavelengths of approx. 0.7m. These networks encompass all the locations of the regional water supply system, except command and control centres.

- With the appropriate modulation algorithm, these kinds of networks provide very reliable transfer of small data packages (packages up to 200 by) between PLCs executing mainly acquisition and control tasks. These networks will have star topology, with a so-called communication centre (CC) in the middle. Each of four networks will have a communication centre, and the locations of these centres will be: storage reservoir R Meševo 1, storage reservoir R Bagdala, hydro press and storage reservoir HPR Mali Šiljegovac and pumping station PS Globare.

- Locations of these communication centres are chosen to meet two criteria: radio-audibility with all objects in belonging network and uniform number of objects per centre/network. PLC in each of communication centres is mastering its radio-modem network and has a full control of traffic over it, at the same time serving as a gateway to wireless Ethernet (WLL) network to which the centre itself belongs.

- The existing CCMS is already exploiting a network of the same kind.

- Wide area network (WAN) based on wireless Ethernet technology (WLL), operating at licence-free 5.4GHz, includes all five command and control centres and four previously listed communication centres. As explained before, the four communication centres are providing interoperability of radio-modem networks and the WLL network.

- The main PLC controller in CCC1 Lipovac, also called Master PLC-1.1, and four PLCs in four communication centres are connected to a separate logic TCP/IP network within WLL. Data transfer between the server and all of monitoring stations in five command and control centres will be conducted over another separate logic TCP/IP, also using WLL.

- Data transfer between the Master PLC-1.1 and PLCs in communication centres over a separate logical TCP/IP network is vital for the operation of entire CCMS. Therefore, the active network equipment will be installed in order to control network traffic and to prioritise messages of this logic network over messages of all other logical networks using the same WLL. It is estimated that this separate logic network will be transferring messages up to 5kB, on average once in every 5s. Although the utilization of this logical network is rather small, that quantity remains inconvenient for radio-modem networks.

- The logical network including the server in CCC1 Lipovac and all the monitoring stations in command and control centres will have higher network load, with messages up to 100kB, on average every 5s and with occasional peaks.

- LAN networks based on Ethernet. Two of these isolated networks already exist, one in the main management building Direkcija and another within the management building of WTP Majdevo, constituting a corporate network of JKP. An LAN will be established within the future CCC1 Lipovac and will connect the Master PLC-1.1, the server and all of the monitoring stations on this site. This new LAN, along with the two existing, will be extended by means of previously described WLL, creating eventually a new corporate network of the public communal company.

- Although the corporate network is not an issue in this project, it must be emphasized that appropriate active network components must provide higher priority of the CCMS messages over all other messages on the corporate network, especially messages on the logic network including Master PLC-1.1 and four PLCs in communication centres. Further expansions of the corporation network are possible.

- Entire Ethernet-based network has a free-topology configuration.

### 1.2.3.2	Survey of network nodes

- The following table lists all of the nodes for four radio-modem networks, anticipated at this stage of CCMS realisation. Each node is shown in the form of PLC's designation and belonging location name.

| No | The communication centres of the radio-modem networks |  |  |  |
| --- | --- | --- | --- | --- |
|  | R Meševo 1 PLC-4.12 | R Bagdala PLC-1.7 | HPR M. Šiljegovac PLC-3.8 | PS Globare PLC-5.23 |
|  | PS Naupare 1 PLC-4.20 | MRS Kruševac PLC-1.9 | PS Gaglovo 2 PLC-3.7 | PS Srnje 1 PLC-5.17 |
|  | R Naupare 1 PLC-4.21 |  | MRS Lipovac PLC-1.5 | R Srnje, PS Krvavica-Padež PLC-5.18 |
|  | PS Naupare 2 PLC-4.22 |  | R Lipovac PLC-1.6 | R Krvavica PLC-5.21 |
|  | R Naupare 2 PLC-4.23 |  | HS Lipovac PLC-1.17 | R Padež PLC-5.22 |
|  | PS Šogolj PLC-4.11 |  |  | PS Srnje 2 PLC-5.19 |
|  | R Meševo 2 PLC-4.13 |  |  | R Srnje 2 PLC-5.20 |
|  | HP Cerova PLC-4.14 |  |  | R Globare PLC-5.24 |
|  |  |  |  | MRS Stalać PLC-1.11 |
|  |  |  |  | MRS Varvarin PLC-1.12 |
|  |  |  |  | MRS Ćićevac PLC-1.13 |
|  |  |  |  | R Todorova kula PLC-1.14 |
|  |  |  |  | R Varvarin PLC-1.15 |
|  |  |  |  | R Ćićevac PLC-1.16 |

- The scope of each radio-modem network is shown on "Communication diagram of CMCS - Radio networks communication centres".

- List of WLL nodes is following.

| - No | - Location | - Node | - Access mode |
| --- | --- | --- | --- |
|  | - CCC1 Lipovac | - Master PLC-1.1 | - Access Point |
|  |  | - Server |  |
|  | - CCC2 Direkcija | - Monitoring stations | - Access Point |
|  | - CCC3 Majdevo | - Monitoring stations | - Subscriber Unit |
|  | - CC4 Bagdala | - Monitoring stations | - Subscriber Unit |
|  | - Communication centre R Bagdala | - PLC-1.7 |  |
|  | - CCC5 Ćelije | - Monitoring stations | - Subscriber Unit |
|  | - Communication centre R Meševo 1 | - PLC-4.12 | - Subscriber Unit |
|  | - Communication centre HPR Mali Šiljegovac | - PLC-3.8 | - Subscriber Unit |
|  | - Communication centre PS Globare | - PLC-5.23 | - Subscriber Unit |
|  | - Relay PS Naupare 1 | - --- | - AP / Backhaul |
|  | - Relay R Krvavica | - --- | - AP / Backhaul |

- Apart form five CCCs and four communication centres, the WLL encompasses two more relays. WLL structure is shown on the "Communication diagram of CMCS - Wireless WAN".

- The new LAN for the CCC1 Lipovac must include Master PLC-1.1, the server and all of the monitoring stations, along with active network equipment. The existing LANs in Direkcija and WTP Majdevo should be equipped with active network devices.

- The entire Ethernet network is shown on "Communication diagram of CMCS - Corporation Ethernet based network". This diagram contains suggested IP addresses for the logic network including Master PLC-1.1 and four PLCs in communication centres, while IP addresses for the server and monitoring stations should be given in accordance with the actual administration policy on the existing LANs.

### 1.2.3.3	Network organisation and operation

- The four radio-modem networks are designed as star-topology networks. Communication masters will be PLCs in communication centres, whilst all other PLCs are communication slaves. These slaves cannot initiate data transfer; they can only send data as a response to master's query. Communication masters in communication centres have a complete control of data traffic on the networks they control.

- Since slaves cannot initiate data transfer and inform master of events as they happen, master must regularly poll each of the slaves in order to ensure real-time operation. Polling must be done every 30s, according to positive experience and the nature of the water supply system. Master PLC of radio-modem network must perform the following:

- Regularly polls all of the communication slaves in its radio-modem network at predefined sample rate, in order to obtain the most recent data and store them temporarily. This way the communication master also becomes a data concentrator for its radio-modem network. According to the adopted serial communication parameters, a single cycle (tick) consisting of master's query and slave's reply should not be longer than 250ms. Tick time must be monitored and timed out, if necessary. After all of the slaves have been polled, the communication master will wait until the beginning of the next sample time period (30s). During this time, the master can only send command messages if required, but not initiate regular polls.

- The communication master occasionally receives command messages by WLL. The master routes these messages towards destination node in its radio-modem network, performing necessary protocol conversion. These command messages have higher priority than regular polls. The communication master cannot initiate command messages on its own, but only route messages obtained via WLL. Command messages tick lasts 250ms; this period is monitored and timed out if no valid response is received within.

- The communication master initiates extra polls following the command message to the same node, in order to obtain command execution status in shortest time possible. These extra polls have higher priority then regular polls. The purpose of this mechanism is to obtain accurate status about previously issued command, as soon as possible.  The extra polls are automatically initiated by the communication master following routed command messages, and data obtained are stored in the same data areas for a location as in the case of regular polls. Extra polls and regular polls use communication tick of the same duration.

- The communication master performs continuous network diagnostics, in order to detect temporary or permanent communication breakdowns, as well as communication recovery towards any slave node. A permanent breakdown is detected after predefined number of successive communication errors.

- Serial communication parameters for radio-modem networks must be 19000bps, 7 data bits, odd parity, 1 stop bit. For the sake of compatibility with the existing CCMS and preventing dependencies on any particular vendor, data protocol used in radio-modem networks is adopted to be MODBUS ASCII version, with necessary support for function codes 03, 06 and 16 (10hex).

- Except from being a communication master of radio-modem networks, each PLC in communication centres performs additional gateway functions between the WLL network and radio-modem networks.

- It sends data gathered by radio-modem network over WLL, in the form of a message to the Master PLC-1.1 in CCC1 Lipovac, after all of the slaves on the radio-modem network have been polled in each 30s communication cycle. The sent data should also include communication statuses for all slaves.

- It sends the data gathered by radio-modem network, along with the communication statuses of slaves, to the Master PLC-1.1 on its particular request. Special care must be taken to maintain data integrity, since the data reception on radio-modem network and Master's request over WLL are asynchronous events.

- Receives command messages over WLL from the Master PLC-1.1 and routes commands to a destination slave on its radio-modem network, performing the necessary protocol conversion and providing that command messages have a higher priority than the regular polls.

- Initiates additional message to Master PLC-1.1 over WLL each time after a command message has been routed from the Master PLV-1.1 on WLL to a slave on the radio-modem network, in order to supply Master PLC-1.1 with the slave's command execution status in the shortest time possible. In the meantime, the communication master should provide response from the targeted slave over radio-modem network.

- In order to avoid dependency on any particular vendor, MOBDUS/TCP protocol is chosen for the logical WLL network encompassing the Master PLC-1.1 and the communication masters in four communication centres (PLC-1.7, PLC-4.12, PLC-3.8, PLC-5.23). The choice of MODBUS/TCP protocol was due to the facts that all versions of MODBUS protocol are publicly documented in detail, the protocol is concise and suitable for real-time applications, the four radio-modem networks within the CCMS will be also using a version of MODBUS protocol, the protocol is widely adopted and used and that nowadays virtually all PLC manufacturers offer support for this protocol. For this application, function codes 03, 06 and 16 must be supported.

- The Master PLC-1.1 and four communication masters in the communication centres will be using TCP/IP transport/address protocol and MODBUS /TCP data format for data interchange over their logical network. The same applies for the logical network between the main server and the Master PLC-1.1, exploiting LAN in the CCC1 Lipovac as its physical layer.

## 1.2.4	The basic CCMS functions

- The CCMS performs two main functions: control and monitoring. Within the scope of monitoring function, the system collects real-time data from all integrated locations, with sample time not longer than 30s, also provides various forms of data presentation, including assistance in alarm and event tracking. The monitoring function also includes database management, which should provide accurate and permanent data archiving in a single database, as well as subsequent data retrieve. Various transducers initiate the monitoring function, whilst PLCs serve as immediate acquisition devices, performing digitalisation and primary data processing.

- PLCs within the four communication centres (R Bagdala, R Meševo 1, HPR Mali Šiljegovac, PS Globare) are data concentrators in the radio-modem networks they control. The Master PLC-1.1 receives all of the data from these four PLCs, becoming thus the main data concentrator unit, containing all technological parameters from the regional water supply system, except for the data from the Ćelije dam.

- The main server of the CCMS regularly reads the real-time data contained in the Master PLC-1.1. The main server is a 24/7 running computer, which receives and stores real-time data from the Master PLC-1.1, performs primary data processing of derived variables, alarms, events or actions, stores data in the integrated database and serves client data requests from the monitoring stations. The main server also acts as a gateway to a logical network connection the Master PLC-1.1 whenever command or parameter change request is issued from a monitoring station.

- The monitoring (operator, supervisory) stations are common PC computers, functionally at the top of chain of command. Since these computers are relieved of archiving or primary data processing tasks, their primary role becomes HMI, i.e. data presentation in various forms (mimic diagrams, lists, reports, trends etc.) and operator interaction (issuing commands, parameter adjustment etc.). The monitoring stations are not crucial for the CCMS, in other words, these stations can be turned on or off at will and the operation of the CCMS will not be imperilled, which is not the case with the main server or the Master PLC-1.1. From the end-user point of view, monitoring stations provide:

- Data presentation,

- Supervisory control,

- Operational control,

- Alarm, event or action tracking,

- User access control,

- Report generation.

- The CCMS control function is distributed between the Master PLC-1.1 and PLCs on each location. Nor the main server neither the monitoring stations have any direct control function, these devices only interact in command messages routing. Especially, monitoring stations provide user interfaces for command issuing or parameter adjustment, but in reality play no part in immediate command execution.

- The PLCs at remote locations are the devices in charge of direct actuator control, in this particular case pump or compressor motors and valve actuators. Based on information obtained directly from transducers and actuators, these PLCs perform additional protective functions towards equipment damage and consumer supply losses, thus maintaining system integrity. In the cases where all of the information necessary for control decision-making is available locally (e.g. some hydro press facilities), control loops are closed within the local PLC and command message obtained via Master PLC-1.1 can only change set points or operation modes.

- The Master PLC-1.1 closes complex control loops, requiring data from several remote locations in the system, typically pairs of downstream pumping station and upstream storage reservoir, or upstream metering and regulation station and downstream storage reservoir. This PLC is continuously getting all the data from the system and therefore possess all the necessary information for control algorithms. The Master PLC-1.1 determines what control actions should be taken by PLC in some remote location and dispatches command message towards it, while the communication masters in the communication centres only mediate in a message delivery.

- The CCMS will be equipped with uninterruptible power supply (UPS) devices with at least 8 hours autonomy time for supplying all transducers, a PLC and a communication equipment on each location. These UPSs will provide active monitoring functions even during extremely prolonged power cuts.

### 1.2.4.1	The main server and monitoring stations

- The SCADA software running on the main server located in CCC1 Lipovac performs the following tasks:

- Takes over the data containing instant measurement values and equipment statuses from the Master PLC-1.1 using LAN. The total amount of data is estimated on 900 digital statuses and 230 analogue values each 30s for the current project stage, or 3700 digital and 700 analogue values every 30s for the complete CCMS.

- Does primary data processing, as well as alarm and event detection.

- Does derived tags processing (totals, aggregate data etc.).

- Provides that time stamped data are regularly stored in the database, sample time not longer than 2min for analogue tags and 30s for digital tags.

- Provides that all the alarms, events and actions are stored in the same database immediately upon the detection, along with the timestamps.

- Records all command orders coming from monitoring stations in the same database immediately upon their reception in the main server.

- Records all system events (access attempts, critical events etc.) in the same database immediately upon detection.

- Sends notification messages to connected and authorised monitoring station in order to inform it about newly detected alarms.

- Serves client requests from connected and authorised monitoring stations for instant data, active alarm, events or actions.

- Serves client requests from connected and authorised monitoring stations for historical data, alarms, events and actions, for arbitrary past time period.

- Executes database processing in order to generate data for aggregate reports, statistical surveys or data exports. This processing is initiated by any authorised monitoring station, and results obtained are sent back to it.

- In the case of grounded requests, routes command messages from authorised monitoring stations to the Master PLC-1.1.

- Resolves command rights between different monitoring stations.

- Performs monitoring station access control and authorisation.

- The monitoring stations in command and control centres are furnished with SCADA software packages, which will provide:

- Access and authorisation to the main server.

- Instant insight into the regional water supply system operation, in the form of mimic diagrams with current values and states, historical trends and lists of alarms, events or actions.

- Basic data management support for valid historical data caching, which will speed up subsequent access and reduce the corporate WAN traffic.

- Initiation of report data generation on the main server and report presentation or print.

- Initiation of statistical data generation on the main server and result presentation.

- User command interface for:

      - Choice between various modes of operation, where available and authorised,

      - Issuing commands to actuators in remote-manual mode of operation, where available and authorised,

      - Parameter adjustment in remote-automatic mode of operation, where available and authorised,

      - Initiation of data export on the main server in selected format and exported data retrieval back to the monitoring station.

### 1.2.4.2	The Master PLC-1.1 basic functions

- The Master PLC-1.1 located in CCC1 Lipovac will be executing the following tasks:

- Serves client requests from the main server either by sending requested data or confirming reception of command messages,

- Analyses command messages from the main server, executes them if possible or routes them towards authorised command centre.

- Serves client requests from the communication masters in one of the four communication centres containing newly acquired data and stores the data in its memory.

- Initiates periodical data requests towards any communication centre if its communication master fails to send fresh data messages for prolonged period.

- Monitors the functionality of logical network on the WLL backbone, encompassing the Master PLC-1.1 and four communication masters (PLC-1.7, PLC-4.12, PLC-3.8, PLC-5.23), and updates communication statuses.

- Accepts and executes command orders changing remote modes of operation, by updating internal mode statuses.

- Closes control loops in remote-automatic mode of operation of hydraulically coupled objects and autonomously sends command messages to targeted PLCs. This means:

      - In the case of a downstream pumping station and an upstream storage reservoir, automatic control means maintaining level in upstream storage reservoir within pair of adjustable limits, providing at the same time that suction reservoir (if any) retains minimal amount of water, defined by another pair of adjustable level limits.  P&I diagram for this case is "P&I diagram of PS and upstream reservoir".

      - In the case of a metering and regulation station and downstream storage reservoir, automatic control means maintaining level in downstream storage reservoir within pair of adjustable limits by valve actuator manipulation, but only in remote automatic level control mode of operation. This mode prevents overflow or emptying of the downstream tank. P&I diagram for this case is "P&I diagram of MRS, downstream reservoir level control scheme". However, metering and regulation stations can be operated in other remote automatic modes of operation, but these modes are handled by local PLCs. The mode of operation choice is up to a system operator.

      - In the case of control variable transducer failure, switches to alternative indicator signals and alternative automatic control algorithms, rising appropriate alarm state.

      - Supports remote manual actuator control by transferring command messages from the main server to a communication centre's PLC, and further to targeted PLC, but only if remote manual mode of operation have been previously selected.

### 1.2.4.3	The PLCs in the communication centres

- As described before, controllers PLC-1.7 (R Bagdala), PLC-4.12 (R Meševo 1), PLC-3.8 (HPR Mali Šiljegovac) and PLC-5.23 (PS Globare) are so-called communication masters of their local radio-modem networks. Apart from the functions of “common” PLCs at remote locations of appropriate type (R, HPR or PS), these controllers should perform several additional communication functions that can be grouped as:

- The local radio-modem network control,

- Gateway functions between the local radio-modem network and the logical WAN with the Master PLC-1.1.

- The aforementioned communication functions have been already described in detail in chapter “Network organisation and operation” of this document.

### 1.2.4.4	The PLCs at remote locations

- The controllers anticipated for pumping stations (PS), hydro press (booster) stations (HP) and storage reservoirs (R) would perform the following functions:

- In the case of R, acquisition of a level transmitter signal, two digital signals of a limit level indicator and a digital signal of auxiliary operating level indicator.

- In the case of PS or HP, acquisition of outlet flow and pressure transmitter signals and digital signals of an outlet pressure limit indicator.

- In the case of PS or HP, acquisition of motors’ statuses.

- For all the locations, acquisition of power supply status, machine room water flooding sensor signal, open door detector signal etc.

- In the case of PS or HP, execution of immediate control and protective actions, mainly towards pump motors. The protective actions specifically include motor protection circuit breaker trip, dry running protection, power shortages, absence of appropriate motor running status feedback and emptying suction reservoir under predefined level limit.

- In the case of HP, autonomous control loop execution in order to maintain outlet pressure within defined limits in remote automatic mode of operation, according to the scheme "P&I diagram of HP".

- Service of the radio-modem network communication, providing regular replies to authorised communication centre's polls and providing relay ("store & forward") functionality with address translation for the protocol adopted.

- Continuous diagnostics including early warning and failure detection for actuators, measurement equipment, communication equipment and controller itself.

- Particularly for pumping stations distant from upstream reservoirs, the belonging PLC will continuously monitor and record duty cycles for all pumps available, as well as an outlet pressure signal for at least 24 hours period, ignoring transient and swift events such as short breaks in duty cycles or abrupt pressure signal changes due to pump start/stop. Such a record, combined with digitally filtered pressure signal, should allow autonomous operation of a pumping station during prolonged communication breakdowns (up to 48 hours), in order to provide emergency water supply while minimising possibility of reservoir spill or discharge. The controllers in pumping stations will:

- Detect a prolonged communication breakdown with an authorised communication centre,

- During communication breakage, autonomously activate pump(s) synchronous to the most recent valid duty-cycle record,

- Upon communication recovery, return to a normal mode of operation, which means that pumps would be driven exclusively by commands from the Master PLC-1.1.

- PLCs anticipated for the metering and regulation station (MRS) will perform the following functions:

- Acquisition of inlet and outlet pressure transducer signals.

- Acquisition of limit pressure indicator signals, open door detector signal, valve chamber water flooding sensor signal, power supply statuses etc.

- Keeping track of actual remote operation mode (remote manual or remote automatic), as well as of remote automatic algorithm - remote automatic flow control, remote automatic pressure control or remote automatic downstream reservoir level control.

- Autonomous control loop execution in the following remote automatic modes: remote automatic flow control or remote automatic pressure control. In both cases, local PLC will manipulate valve actuator in order to maintain the controlled variable (either flow or pressure) at its set point. The control scheme is shown on "P&I diagram of MRS, pressure or flow control scheme".

- Valve positioning according to command orders coming from the Master PLC-1.1 in a remote automatic mode used to control downstream reservoir water level, scheme "P&I diagram of MRS, downstream reservoir level control scheme".

- Valve positioning according to command orders obtained from the Master PLC-1.1 in a remote manual mode of operation.

- Immediate protective functions on valve actuator motors.

- Service of the radio-modem network communication, providing regular replies to authorised communication centre's polls and providing relay ("store & forward") functionality with address translation for the protocol adopted.

- Continuous diagnostics including early warning and failure detection for actuators, measurement equipment, communication equipment and controller itself.

## 1.2.5	The CCMS monitoring functions

- All monitoring stations' SCADA software must be provided with:

- Three logical levels of mimic diagrams:

      - Mimic diagrams for each subsystem within the regional water supply system, indicating main measurements and statuses (reservoir levels, flows and pressures, grouped motor statuses).

      - Mimic diagrams for each distribution network (DN), indicating all measurements and statuses, but without command interface.

      - Mimic diagrams for each:

      - pair of a downstream pumping station and an upstream reservoir,

      - pair of a metering and regulation station and a downstream reservoir,

      - hydro press (booster) station,

      - specific locations such as MRS Kruševac or HS Lipovac.

- with all measurements and statuses, along with a user interface for issuing commands and parameter adjustment.

- On a mimic diagram with a command interface, the latter must provide:

      - Operation mode selection, for each PS, HP or MRS separately.

      - In remote manual operation mode, issuing of the following immediate commands:

- turn on/off each pump motor,

- abnormal operating conditions acknowledgement,

- set up valve position for each valve in a MRS,

- turn on or off autonomous chlorine dosage equipment in a HS, if such a possibility exists for the equipment in question.

      - In remote automatic operation mode, set-up of:

- outlet pressure set point for a HP with frequency inverters,

- flow or pressure set point for a MRS, depending on active automatic control algorithm,

- chlorine dosage set point in a HS, if such a possibility exists for the installed chlorinator.

      - In remote operation mode, set-up of:

- level limits in upstream and suction reservoirs for remote automatic operation of a PS,

- outlet pressure limits for remote automatic operation of a HP,

- downstream reservoir level limits for remote automatic operation of a MRS with activated downstream level control algorithm.

- Possibility of tracking alarm trips (on and off) and alarm acknowledgements.

- Possibility of operator actions tracking, especially command actions.

- Surveys of historical data in form of trends and also alarm, action or event lists, either on screen or in the form of printout.

- Possibility of report generation for a separate subsystems or distribution networks:

      - single shift reports,

      - daily reports,

      - monthly reports,

      - yearly reports.

      - Possibility of initiating and presentation of statistical data processing.

      - Possibility of historical data export in selected format.

      - User interface for access control and authorisation.

### 1.2.5.1	The monitoring function distribution

- The monitoring function distribution among monitoring stations in command and control centres in a sense of jurisdiction over objects, follows public company's organisation scheme. The distribution is as follows:

| - CCC | - Monitoring allowed for |
| --- | --- |
| - CCC1 Lipovac | - All the locations of all subsystems - Ćelije dam - WTP Majdevo |
| - CCC2 Direkcija | - All the locations of all subsystems - Ćelije dam - WTP Majdevo |
| - CCC3 Majdevo | - All the locations of subsystem "The Regional system" - All the locations within DN Majdevo - All the locations within DN Aleksandrovac - All the locations within DN Nabrđe - Ćelije dam |
| - CCC4 Bagdala | - All the locations of subsystem "The II Supply Zone System" |
| - CCC5 Ćelije | - All the locations of subsystem "The Regional system" - WTP Majdevo |

## 1.2.6	The CCMS control functions

- The system main resources, pump motors and valve actuators, can be controlled in two ways:

- Locally, using switches on motor control cabinets (MCC) located in the vicinity of the equipment, in which case the CCMS has no authority,

- Remotely, when the CCMS has full control over the equipment.

- The mode selection will be done by a special switch on the motor control cabinet on each location separately. This project anticipates reconstruction of nearly all motor control cabinets in PSs and HPs in order to integrate them into the CCMS. The reconstruction means:

- Installation of rotary multi-pole 3-position switch 1-0-2 meaning "Local-0-Remote", which should provide operating mode selection or shutdown of all drives if in position "0". Where not applicable due to poor condition or confined space of the MCC, the switch might be installed onto a new CCMS distribution cabinet ROMTK, originally intended for controller and communication equipment.

- Motor control circuitry modification in order to:

      - incorporate dry running protection, motor protection circuit breakers and 3 phase AC line monitors, both in local and remote operation modes,

      - incorporate remote switching in remote operation mode by voltage-free contacts from ROMTK, for each pump separately,

      - provide that remote switching has no effect in local operation mode,

      - provide that local switching has no effect in remote operation mode. This refers to local motor start pushbuttons/switches and particularly to local automation logic such as upstream reservoir operation level switches, outlet pressure switches etc.

      - provide switches for duty pump(s) selection in remote operation mode.

      - Installation of auxiliary contacts, relays, wire terminals and clamps necessary for providing status signals to the ROMTK within the CCMS. Status signals should include:

      - power statuses,

      - motor statuses, including those from motor protective devices,

      - operation mode selection switch "Local-0-Remote" statuses,

      - duty pump selection switches' statuses,

      - dry running protection status,

      - upstream reservoir operating level signals, if any,

      - outlet pressure switches' signals, if any,

      - other statuses available in MCC (e.g. from pressure limit indicators, level limit indicators etc).

- For the time being, the most widely used operation modes in public communal company JKP Vodovod - Kruševac are local ones, except for the locations already integrated into the existing CCMS, where remote automatic operation mode is used. In the future, local operation modes will be used only during object commissioning or regular maintenance, while the remote operation modes will be the most common.

- The remote mode of operation has two options:

- Remote manual operation mode. In this mode, an operator can issue direct commands concerning pumps in PSs or valve position in MRSs, via monitoring stations in the command and control centres. The command messages are routed to the target controllers, which, in turn, execute them. All command can be executed proviso that all the operating conditions are regular. In this mode, an operator takes all the responsibility for the locations considered, whilst the CCMS only transmits the commands. However, all the protective functions are active in remote manual operation mode in order to prevent equipment damage.

- Remote automatic operation mode. In this mode an operator can only adjust set points, e.g. level limits in an upstream reservoir, or flow set point for a MRS, but cannot issue direct commands such as turning on/off a pump. In this operation mode, the CCMS has full control over the regional water supply system and generates commands itself, while an operator can only perform supervisory control. All the protective functions remain active in this mode.

- An operator can select between these two options of remote operation mode at any time, for each pumping station or metering and regulation station separately. This makes the system flexible, since only some parts of the system can be operating in remote automatic mode, while the others can be temporarily in local modes, due to e.g. reconstruction, regular maintenance, or simply because not yet being integrated into CCMS.

### 1.2.6.1	Control actions coordination

- At any moment, command directives and parameter adjustment for a single location or a subsystem within the regional water supply system can only be done from a single monitoring station in the CCMS. This way, collisions that might appear as a result of issuing contradictory commands from different monitoring stations are avoided. The monitoring stations, the main server and, if necessary, the Master PLC-1.1, will be equipped with a software mechanisms which will provide that only one monitoring station has command jurisdiction over a single object or a subsystem at any given time.

- If several operators with command privileges for the same subsystem are logged onto the CCMS at the same time, only one of them will have executive command rights. If, for any reason, another operator is to be assigned these rights, he (or she) will have to activate a special function on his (her) monitoring station requesting executive command rights for a location or a subsystem of interest. Only after the right has been granted, this other operator will be allowed to command or adjust parameters concerning the selected location or subsystem. All other operators currently logged onto the CCMS will be informed about such an action. Additionally, not all of the monitoring stations can be used for the entire system control, depending on which command and control centre they belong to.

| - CCC | - Command jurisdiction over |
| --- | --- |
| - CCC1 Lipovac | - All of the locations in the system |
| - CCC2 Direkcija | - All of the locations in the system |
| - CCC3 Majdevo | - The locations within DN Majdevo, DN Aleksandrovac and DN Nabrđe |
| - CCC4 Bagdala | - The locations within DN Šumice |
| - CCC5 Ćelije | - None of the locations in the system |

- The CCMS will keep a track of executive command rights takeover along with other operator actions and they will remain permanently recorded in the database on the main server.

## The CCMS equipment placement

- The CCMS equipment at each remote location should be placed in a separate distribution cabinet (ROMTK) of high-degree protection. This particularly includes:

- controller equipment,

- communication equipment, except for antenna systems,

- measuring equipment. This specially holds for flow meters, level and pressure measuring devices, which must be completely installed in the cabinets, while belonging display units must be door mounted. Only sensor parts of the measuring devices are excepted from this, since they must be installed directly into the storage reservoirs or on the pipelines,

- various indicators, except for the sensors, which will be installed directly into the reservoirs or on the pipelines,

- uninterruptible power supply, including batteries,

- auxiliary equipment such as switches, interface relays, fuses, interior lighting, anti-condensation heater etc.

- The distribution cabinets should be indoor wall mounting, protection class IP54. On the locations with poor ventilation and high relative humidity, the cabinets must be equipped with open door detector integrated into the CCMS to help prevent equipment deterioration due to humidity exposure.

- The various equipment inside the ROMTK cabinet must have the following power supply levels:

- controller equipment 24VDC

- communication equipment 24VDC or 12VDC (both radio and WLL equipment),

- all the measuring equipment 24VDC (flow, level and pressure transducers),

- all the indicators 24VDC.

- The requirements concerning the equipment placement, an UPS system and power supply levels also apply for controller and communication equipment in CCC1 Lipovac, CCC3 Majdevo and CCC4 Bagdala.

- Other equipment in command and control centres will be located in control rooms, except for communication and active WLL network equipment, which will be placed into separate distribution cabinets nearby monitoring stations. Communication and active network equipment in the command and control centres, as well as the main server, must be supported by the appropriate UPS systems.

### 1.2.7.1	Uninterruptible power supply systems

- Although power cuts happens only occasionally, usually targeting small areas covered by regional water supply system, it is vital that the CCMS functions normally even in these conditions. Therefore, all the equipment in the ROMTK cabinet anticipated for DC power supply will be supported by an UPS system.

- UPS system must be installed inside the ROMTK cabinet, together with two sealed lead acid maintenance-free rechargeable batteries, capacity at least 18Ah. UPS will be powered by 220VAC and must provide two controlled, backed up DC outputs, 24VDC and 12VDC, with total capacity enough to run all previously listed equipment for not less than 8 hours.

- The exceptions are UPS systems for the main server in CCC1 Lipovac and monitoring stations in the command and control centres. These UPS systems will have shorter autonomy, less harsh operating conditions and power levels suitable for the supported computer equipment.

## 1.2.8	The data available through the CCMS

- All the data available through the CCMS are listed in the next part of this documentation, for each location that will be included in the first stage of CCMS realisation. Signal tables can be found in sections named "Equipment and labour required for integration into the CCMS".

- The total number of data stored on the main server is estimated to 900 digital and 230 analogue signals for the first stage, or 3700 digital and 700 analogues for the complete CCMS. These numbers include not only raw PLC inputs and outputs, but also derived statuses and control parameters. However, they don't include variables generated by the server, such as flow totals, pumps' total hours, aggregates etc.

## 1.2.9	The CCMS software

- Only the application software essential for the CCMS operation will be considered:

- The Master PLC-1.1 application software,

- Application software for the PLCs at remote locations, except for the communication centres,

- Application software for the PLCs in the communication centres,

- The main server's application software,

- The monitoring stations' application software.

- PLC system software or PLC development software tools are considered parts of a controller equipment and will not be an issue in this documentation. The same applies for the operating system software (OS) of the main server and monitoring stations, except that chosen OS must be compatible with ones already installed within the existing CCMS.

- Software support for the measuring and communicational equipment is considered a part of it and will not be considered separately.

### 1.2.9.1	The Master PLC-1.1 application software

- The Master PLC-1.1 application software must provide the following:

- Communication functions:

- client/server communication services providing data exchange with PLCs in the communication centres (PLC-1.7, PLC-4.12, PLC-3.8, PLC-5.23),

- client/server communication services providing data exchange with the main server,

- the main server command message analysis, which yields:

      - in the case of coupled objects where the Master is in charge of remote automatic operation, memorising data concerning this mode, such as operation mode or automatic control parameters, in the Master's main storage area,

      - in the case of a message concerning object in remote manual mode or object which handles automatic mode autonomously, message routing to the authorised communication centre, where it will be further dispatched to the targeted PLC,

      - monitoring and diagnostics of the logical WLL connecting the Master and four PLCs in communication centres;

- Monitoring functions:

- keeping main storage area with the most recent data from the entire regional water supply system, not older than 30s, including communication statuses. Data quantity estimation is given earlier in the document.

- Control functions:

- keeping track of remote operation mode (manual or automatic) for each PS, HP or MRS. For a HP or a MRS, this information is also routed to the targeted PLC,

- permits messages requesting direct pump motor actions only for those PSs or HPs in remote manual operation mode,

- permits messages requesting direct valve positioning only for MRSs in remote manual oepration mode,

- accepts an aggregate status, indicating abnormal operating conditions, from any remote location and prevents further control actions for the object as long as the status remains active,

- allows a message, requesting the abnormal operating condition status acknowledgement, to be dispatched towards targeted object. The acknowledgement is essentially a permission to continue operation, provided that operating conditions have already been normalised,

- accepts upper and lower level limits for an upstream reservoir level control and stores them into the main storage area,

- dispatches a message containing lower and/or upper protective level limits for the suction reservoir towards targeted PS or HP,

- autonomously sends command messages requesting immediate pump actions for the pump stations in remote automatic operation mode. The command messages are generated as a result of comparison of a level measurement and two aforementioned level limits for each upstream reservoir in the system. This algorithm is executed proviso that there has been normal communication with all relevant objects within the last 30s and that normal operation conditions are present in the downstream pumping station.

- autonomously sends command messages requesting immediate valve positioning for metering and regulation stations in remote automatic operation mode with downstream reservoir level control algorithm selected. The new valve position is determined periodically, at least once each 6 hours, using the downstream reservoir level measurement and level limits, but only if there has been normal communication with all relevant objects within the last 30s and that normal operation conditions are present in the upstream metering and regulation station.

- switches to upstream reservoir's level indicator signals if level transmitter fault has been previously detected, but only in remote automatic operation mode of downstream pumping station,

- aborts valve position manipulation in a metering and regulation station if a fault has been previously detected with the downstream reservoir level transmitter, but only if downstream reservoir level control algorithm has been active for the downstream MRS,‚

- switches to outlet pressostat signals if outlet pressure transmitter fault has been previously detected, but only in remote automatic operation mode of hydro press facilities.

- Diagnostic functions:

- constantly performs self-diagnostic tests and places results in the main storage area.

### 1.2.9.2	The application software for PLCs at remote locations

- The application software for all the PLCs, except for the PLCs in the communication centres and the Master PLC-1.1, must do the following:

- Communication functions:

- services data requests from the authorised command centre on the radio-modem network and sends replies with the most recent data,

- receives command messages from the authorised command centres and sends back acknowledgement messages,

- provides relay functionality ("store & forward") with an address translation table in a separate permanent memory area.

- Monitoring functions:

- does primary data processing, i.e. averaging, filtering, latching and temporary data archiving in a continuous storage area. This particularly holds for signals representing events faster in their nature than normal sample rate of 30s, like door openings, short-term actuator activations, short power cuts, pressure indicator trips etc.

- Control and protective functions:

- in the case of a PS or a HP, executes direct commands to actuators, taking care of elapsed time between a motor restarts, making necessary delays to avoid simultaneous motor starts where applicable, equalizing pump loads by regular switching of duty and standby pumps where possible etc.,

- in the case of a PS or a HP, executes motor protection functions,

- in the case of a PS or a HP, autonomously turns off the pump motors if water level in suction reservoir drops below the lower protection limit, activating the abnormal operating condition status. After the water level in a suction reservoir rises above the upper protection limit, the software deactivates the abnormal operation condition status,

- in the case of a PS or a HP, activates the abnormal operating condition status in the following situations:

      - not enough water in a suction reservoir,

      - power outage,

      - dry running protection trip,

      - motor protection circuit breaker trip,

      - motor running status confirmation is missing after the run command has been issued,

      - motor running status still active after the run command has been cancelled,

      - faulty manipulation of the MCC switches in remote operation modes,

      - outlet pressure too high.

- In the first two cases, abnormal operating condition status is autonomously reset upon condition normalization; in all other cases both condition normalization and an acknowledge command message are required.

- in the case of a PS or a HP, accepts a request for the abnormal operating condition status acknowledgement. The acknowledgement is essentially a permission to continue operation, provided that operating conditions have already normalised. This operation can also be performed by manipulation of the "Local-0-Remote" switch on the MCC, on each transition of the switch into position "Remote",

- in the case of a PS or a HP, records pumps' duty cycles for the last 48 hours, ignoring transient or swift events (i.e. short breaks or short-term runs) and synchronises this record in real-time,

- in the case of a PS or a HP, monitors a prolonged communication breakdown and if detected, performs autonomous pump(s) activation according to synchronised pumps' duty cycle record. After the communication has been restored, continues with the normal operation obeying exclusively commands from the Master PLC-1.1,

- in the case of a HP equipped with a frequency inverter, closes the outlet pressure control loop and maintains the pressure within defined limits by varying pump motor speed. The pressure limits are adjustable via command messages coming from the Master PLC-1.1,

- in the case of a MRS, executes direct control actions on a valve actuator, taking care of elapsed time between the actuator motor restarts, specially when changing rotation direction,

- in the case of a MRS, executes valve actuator protection functions,

- in the case of a MRS, activates the abnormal operating condition status in the following situations:

      - power outage,

      - valve position transducer failure,

      - motor protection circuit breaker trip,

      - valve torque switch trip,

      - not reaching the specified valve position in maximally allowed trip time.

- In the case of power loss, abnormal operating condition status is autonomously reset upon power restoration; in all other cases both condition normalization and an acknowledge command message are required.

- in the case of a MRS, accepts a request for the abnormal operating condition status acknowledgement. The acknowledgement is essentially a permission to continue operation, provided that operating conditions have already normalised. This operation can also be performed by manipulation of the "Local-0-Remote" switch on the MCC, on each transition of the switch into position "Remote",

- in the case of a MRS, keeps track of operation mode and selected remote automatic control algorithm,

- in the case of a MRS, accepts a command message for the active regulation valve selection, since only one valve is allowed to be active at all times,

- in the case of a MRS, closes the active valve position control loop in all remote operation modes,

- in the case of a MRS, continuously monitors the active valve position transducer and in the case of its failure, breaks the control loop preventing senseless valve position changes,

- in the case of a MRS, closes flow control loop in remote automatic mode, but only if flow control algorithm has been selected. The flow control loop will be cascaded to the valve position control loop, while flow set point value will be set by an appropriate command message,

- in the case of a MRS, closes pressure control loop in remote automatic mode if pressure control algorithm has been selected. The pressure control loop will be cascaded to the valve position control loop, while pressure set point value will be set by a command message,

- for all the locations, monitors the functionality of all the transducers and in the case of failure switches to redundant indicators and alternative control algorithms, tripping the alarm statuses. This particularly holds for a suction reservoir level sensor in a PS or a HP or an outlet pressure sensor in a HP.

- Diagnostic functions:

- constantly performs self-diagnostic tests and trips an alarm if irregularity has been detected,

- constantly compares transducer and indicator signals concerning the same or related physical variables and trips an early warning alarm when they are in conflict:

      - motor operation statuses and outlet flow signal should be correlated,

      - a level transducer signal should be in accordance with level indicators,

      - a pressure transducer signal should be in accordance with pressure indicators,

      - constantly monitors for abrupt, unrealistic changes of transducer signals (e.g. level or flow changes) and triggers alarms accordingly,

      - constantly monitors transducer signals for physically impossible measurement values and triggers alarms accordingly,

      - constantly checks broken wire situation for all analogue measurements, which are represented by standard 4-20mA signals, and triggers alarms accordingly,

- Special functions:

- in the case of a HS, does not perform any direct control action, since the dosage equipment is operating autonomously. The only exception might be converting the chlorine dosage set point value, obtained through a command message, into a 4-20mA signal and supplying it into the dosage equipment, if applicable.

### 1.2.9.3	The application software for PLCs in communication centres

- The application software of so-called communication masters in the four communication centres (PLC-1.7 in R Bagdala, PLC-4.12 in R Meševo 1, PLC-3.8 in HPR Mali Šiljegovac and PLC-5.23 in PS Globare) should include all monitoring, control, protective and diagnostic functions previously described for a location of appropriate type. However, its communication functions are different and they must provide the following:

- regular polling of all the communication slaves in a radio-modem network controlled by the communication centre, at sample rate of 30s,

- updating slave communication statuses, including temporary and permanent communication breakdowns,

- keeping the most recently obtained data from the slaves in a storage area, together with IO signals obtained directly through its own IO modules,

- sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL, after all of the slaves have been polled in each 30s communication cycle,

- sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request, maintaining data integrity,

- reception of command messages from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network. The command messages have higher priority than regular polls,

- sending an additional poll to the slave previously targeted by a command message in order to provide command execution status in the shortest time possible. These additional polls have higher priority than regular polls,

- sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL. This way the Master PLC-1.1 obtains the response to a given command as quickly as possible.

### 1.2.9.4	The main server application software

- The main server application software must ensure 24/7 server operation. The software functions encompass:

- Communication functions:

- client/server communication to the Master PLC-1.1 over a separate logical LAN, using adopted data format,

- periodical retrieve of real-time data from the Master PLC-1.1,

- sending notification messages to the monitoring stations upon the new alarm detection,

- sending data upon monitoring stations' data request, either the most recent data or historical data,

- reception of manually entered data, typically results of laboratory analysis, from the monitoring stations,

- reception of command messages from the monitoring stations, access rights verification and message routing to the Master PLC-1.1,

- Data processing and archiving functions:

- processing of aggregate variables, such as various totals, sums etc.,

- limit and rate alarm detection,

- keeping record of alarm state transition, activation, deactivation and acknowledgement, in the integrated database,

- keeping record of events and operator actions in the integrated database,

- archiving of all retrieved real-time data, aggregate data and manually entered data in the integrated database,

- database integrity protection, by preventing record deletion or change and allowing only new record insertion,

- data management utilities such as data search for an arbitrary variable set or time period. In this case, the data means all measurements, control parameters, digital signals, alarms, events or actions,

- generation of aggregate periodical or statistical reports, alarm, event or action reports etc. for an arbitrary time period,

- possibility of on-line acquisition parameter change, specifically measurement ranges, measurement alarm levels and digital alarm definitions, along with keeping track of these changes in the integrated database,

- possibility of archived data export in predefined formats;

- Utility services:

- keeping track of all operator command actions in the integrated database, namely control or acquisition parameter changes, operation mode changes, remote manual mode commands, access attempts, alarm acknowledgements, administrative actions, manual data entries, execution command rights requests etc.,

- execution of several types of command messages from the monitoring stations: acquisition parameter changes, alarm acknowledgements, log on/off requests, administrative requests, and manual data entries. All other command messages are routed to the Master PLC-1.1,

- Other functions:

- access control. The server will reject all requests from the computers not being registered as the CCMS monitoring stations,

- user privilege management. In the CCMS at least three privilege levels are necessary: a) monitoring level, b) monitoring and control level and c) monitoring, control and administration level,

- administrative tools, which allow access parameter control, user accounts management and monitoring station registry management.

### 1.2.9.5	The monitoring station application software

- The application software for each monitoring station must provide:

- Data presentation and command interface:

- mimic diagrams of:

      - subsystems,

      - distribution networks,

      - all pairs of a downstream pumping station and an upstream reservoir,

      - all pairs of a metering and regulation station and a downstream reservoir,

      - all hydro press (booster) stations,

      - all specific locations such as MRS Kruševac or HS Lipovac.

- containing all relevant information. Total number of mimic diagrams for the entire CCMS is estimated to be 88,

- a command interface must provide:

      - Operation mode selection, for each PS, HP or MRS separately,

      - Control algorithm selection for each MRS,

      - In remote manual operation mode, issuing of the following direct commands:

- turning on/off each pump motor,

- duty pump selection, if applicable,

- acknowledgement of abnormal operating condition status,

- active valve selection for each MRS,

- set up valve position for each valve in a MRS,

- turn on/off autonomous chlorine dosage equipment in a HS, if applicable.

      - In remote automatic operation mode, set-up of:

- outlet pressure set point for a HP with a frequency inverter,

- flow set point for a MRS, if flow control algorithm is active,

- pressure set point for a MRS, if pressure control algorithm is active,

- chlorine dosage set point in a HS, if applicable;

      - In remote operation mode, set-up of:

- level limits in an upstream reservoir for remote automatic operation of a PS,

- level limits in a suction reservoir for remote automatic operation of a PS or a HP,

- outlet pressure limits for remote automatic operation of a HP,

- downstream reservoir level limits for remote automatic operation of a MRS with activated downstream level control algorithm;

- archive data presentation:

      - trends, with at least 4 simultaneously presented variables on separate graphs on a single screen, with possibility of time axis adjustment, ordinate adjustment and time synchronization,

      - alarm lists, with indicated activation time, deactivation time and acknowledgement time, as well as alarm description, origin and cause, for any given time period,

      - event lists, with indicated time, description and origin, for any given time period,

      - action lists, with indicated time, description and operator identification, for any given time period. The event and action lists may be joined together,

      - available printouts of trends or any aforementioned lists,

      - necessity of efficient navigation through mimic diagrams.

- Report generation:

- Initiating report generation for each subsystem or distribution network:

      - single shift reports,

      - daily reports,

      - monthly reports,

      - yearly reports,

      - periodical reports, where applicable, for any given time period.

      - available printouts of generated reports,

      - possibility of initiating and presentation of statistical reports for any given time period,

- Communication functions:

- server communication services towards the main server for alarm notification reception,

- client communication services towards the main server for data access,

- client communication services towards the main server for command messaging,

- client communication services towards the main server for manually entered data submission,

- Special functions:

- user interface support for

      - acquisition parameter change,

      - system access,

      - administrative functions,

      - manual data entries,

      - support for a local database, related to all the objects and/or significant peaces of equipment, with possibility of storing photos, graphics and texts for each related object. The purpose of this database is to store additional data, apart from those reaching the CCMS through the acquisition equipment. This base is correlated neither to the main server database nor to any other database. It is managed only locally, data is entered manually and it suites to station operator needs. Typically contains maintenance records, technical details, management remarks, personal records etc.

      - basic data management support for caching valid historical data, previously obtained from the main server, in order to speed up subsequent data access and reduce network traffic.

- The application software configuration must follow the monitoring and control functions distribution among the command and control centres, as summarised in the following table:

| - CCC | - Monitoring allowed for | - Command jurisdiction over |
| --- | --- | --- |
| - CCC1 Lipovac | - All subsystems - Ćelije dam - WTP Majdevo | - All the locations in the system, - except for the Ćelije dam |
| - CCC2 Direkcija | - All subsystems - Ćelije dam - WTP Majdevo | All the locations in the system, except for the Ćelije dam |
| - CCC3 Majdevo | - Subsystem "The Regional system" - All the locations within DN Majdevo All the locations within DN Aleksandrovac All the locations within DN Nabrđe Ćelije dam | Only the locations within DN Majdevo, DN Aleksandrovac and DN Nabrđe |
| - CCC4 Bagdala | Subsystem "The II Supply Zone System" | Only the locations within DN Šumice |
| - CCC5 Ćelije | Subsystem "The Regional system" WTP Majdevo | None of the locations in the system |

II.	TECHNICAL AND OPERATIONAL CHARACTERISTICS

# 1.3	The Subsystem "The Regional System"

## 1.3.1	The Command And Control Centres

- Five command and control centres (CCC) are anticipated within "The Regional System" within the CCMS of the regional water supply system Ćelije.

- CCC1 Lipovac, the future main centre, in the design phase,

- CCC2 Direkcija, the existing operational centre and in the future alternative centre to the CCC1,

- CCC3 Majdevo, the existing local centre,

- CCC4 Bagdala, the existing local centre,

- CCC5 Ćelije, the existing local centre.

### 1.3.1.1	The CCC1 Lipovac

Present situation

The command and control centre CCC1 Lipovac will be established in the main maintenance facility of JKP company, in village Lipovac, nearby metering and regulation station MRS Lipovac. The centre is in the design phase.

The centre's primary role is to ensure normal operation of the regional water supply system, i.e. to provide coordination of hydraulically coupled distant locations, which is necessary for regular water supply. CCC1 Lipovac will also play an important role in the system maintenance, since many of the information concentrated in the centre are relevant for it. Therefore, the coordination of the centre and the maintenance department will be very important for the continuous regular water supply to such wide consumer area.

The last but not the least, this CCC1 will be information centre with a database containing real-time technological measurements and events for a long period, providing a valuable tool for the regional system development.

All these functions should eventually improve water supply system and reduce water transportation and maintenance costs.

Until CCC1 establishment, CCC2 Direkcija remains the main command and control centre in the existing CCMS and the entire water supply system.

Equipment and labour required for CCC1 integration into the CCMS

Requirements for establishment and integration of CCC1 Lipovac into the CCMS are:

- To construct and furnish the future centre premise,

- To provide access from the CCC1 to logical WLL used by CCMS. Network will connect the four communication centres R Bagdala, R Meševo 1, HPR Mali Šiljegovac and PS Globare and all five command and control centres. This further means:

- to provide data transfer over the network, using previously defined protocols,

- to install wireless Ethernet equipment and a router,

- to install over voltage protection devices,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment.

- To establish an Ethernet LAN within the CCC1, which will connect the main server, monitoring stations and the Master PLC-1.1. This further means:

- to install an appropriate network switch,

- to do a necessary UTP wiring inside the CCC1 premise between the Master PLC-1.1, the main server, monitoring stations and a switch,

- to install other passive network equipment,

- To install a new distribution cabinet for the CCMS, named ROMTK. The cabinet will contain:

- the Master PLC-1.1 controller,

- network equipment, both for the LAN and the WLL, together with protective devices,

- UPS system, including batteries,

- other auxiliary equipment;

- To equip the Master PLC-1.1 with:

- an Ethernet communication module with the socket TCP/IP support,

- the application software providing:

  - client/server communication with all communication centres and the main server,

  - concentration of all regional system real-time data in a main data storage memory area; data are updated each 30s,

  - control loop closing for all pairs of hydraulically coupled objects, in order to provide fully remote automatic operation mode,

  - analysis and verification of command messages obtained from the main server, followed by:

    - data storage of control parameters, which remains in the Master's memory, such as operation modes, upstream reservoir level limits etc.

    - otherwise, message routing to authorised communication centre.

  - diagnostic functions for the logical WLL with command centres and Master itself.

- To install a PC computer which will serve as the main server, capable of 24/7 operation, with raid disks providing increased data security, LAN support, an optical DVD drive, standard UI interfaces, UPS with 1 hour autonomy and over voltage and surge protectors,

- To install six PC computers that will be monitoring stations, each intended for one of the six regional water supply subsystems. The computers must be fitted for 24/7 operation, with high resolution monitors 22", LAN support, UPS systems with at least 30min autonomy and over voltage and surge protectors,

- To install the main server application software in order to provide:

- two-way client/server communication with the Master PLC-1.1, using LAN and the adopted data format,

- regular real-time data retrieve from the Master PLC-1.1 and data archiving in the internal database,

- update of aggregate data,

- alarm tracking and detection, insertion into the internal database,

- monitoring station notification upon new alarm detection,

- service of monitoring stations' data requests, including requests for the most recent or archived data, as well as for alarms, events or actions,

- reception of manually entered data (e.g. lab analysis results) and their storage in the internal database,

- reception of monitoring stations command messages, executive command rights verification, action recording in the database, command execution or routing to the Master PLC-1.1,

- statistical or periodical report generation according to the monitoring stations requests,

- three levels of authorisation: a) monitoring level, b) monitoring and control level and c) monitoring, control and administration level,

- on-line acquisition parameter change, specifically measurement ranges, measurement alarm levels and digital alarm definitions, tracking of changes in the database,

- archived data export in predefined formats;

- To install monitoring stations' application software in order to provide:

- the actual process information presentation. Each of six monitoring stations will be visualising one of the six regional water supply subsystems. Visualisation must be provided through a three levels of mimic diagrams showing:

    - the entire subsystem, without control possibilities, but with the essential technological information,

    - each distribution network, without control possibilities, but with all technological information for the subsystem considered,

    - pairs of hydraulically coupled objects-locations, or single hydraulically self-sustained objects, with all available information and command interface.

Number of mimic diagrams for the entire CCMS is estimated to 88.

- the internal database access and data presentation in the form of:

    - trends, with at least 4 simultaneously presented variables on separate graphs on a single screen, with possibility of time axis adjustment, ordinate adjustment and time synchronization,

    - alarm lists, with indicated activation time, deactivation time and acknowledgement time, as well as alarm description, origin and cause, for any given time period,

    - event lists, with indicated time, description and origin, for any given time period,

    - action lists, with indicated time, description and operator identification, for any given time period. The event and action lists may be presented simultaneously as a single list,

    - any trend or list printout,

- initiation of statistical report generation and its presentation,

- initiation of periodical report generation and its presentation or print. The number of periodical reports (shift, daily, monthly, yearly) is estimated as:

| Subsystem | Number of reports |
| --- | --- |
| - The Regional System, | 5 |
| - The II Supply Zone System, | 1 |
| - The System East, | 7 |
| - The Rasina Wally System, | 10 |
| - The System West - Župa, | 6 |
| The Morava System. | 6 |

- user interface for

    - issuing commands,

    - control parameter change within predefined absolute limits,

    - acquisition parameter change,

    - system access,

    - administrative functions,

    - manual data entries,

- To install a printer connected to the main server, and make it available to all monitoring stations within the LAN.

The aforementioned equipment and labour will be sufficient for establishment and integration of CCC1 Lipovac into the CCMS.

### 1.3.1.2	The CCC2 Direkcija

Present situation

The CCC2 Direkcija is the main operational command and control centre in the existing CCMS, located in main management building of public communal company JKP Vodovod. The main server and monitoring stations are equipped with SCADA packages "MapNet+". A PLC controller CJ1M-CPU13 ETN, playing a role of the Master PLC, and a radio base station T96-SR, serving the existing radio-modem network, are also installed.

- This stage of the project anticipates the removal of the PLC form CCC2 Direkcija to CCC3 Majdevo, where it will be turned into PLC-1.3. The command and control centre CCC2 will remain in the new CCMS as a supervisory centre with possibility of alternative control of any part of regional water supply system. However, in the new CCMS this command and control centre will become mainly developmental and planning centre, while the CCC1 will take over the operational control of the regional water supply system.

Equipment and labour required for CCC2 re-integration to the new CCMS

CCC2 Direkcija is already integrated into the existing CCMS. In order to adapt its present state into the new CCMS, the following is required:

- To construct and furbish new premises for the CCC2 within the main management building Direkcija, instead of temporary used offices,

- To provide access from the CCC2 to logical WLL used by CCMS, which means:

- to provide data transfer over the network, using previously defined protocols,

- to install wireless Ethernet equipment and a router,

- to install over voltage and surge protection devices,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment,

- to physically connect the existing LAN in the CCC2 premises to the new WLL used by CCMS.

- To install a PC computer in the Technical manager's office, which will be a new monitoring station fitted for 24/7 operation, with a high resolution monitor 22", LAN support, a UPS system and an over voltage/surge protector,

- To re-configure two SCADA packages that has already been installed on the two existing monitoring stations, and to install a compatible new SCADA instance onto the new monitoring station, in order to provide full monitoring and control capabilities for the entire regional water supply system from this CCC. This will be achieved by:

- number of mimic diagrams for

    - the each subsystem with the essential technological information,

    - each distribution network with all technological information considered,

    - pairs of hydraulically coupled objects-locations, or single hydraulically self-sustained objects, with all available information and command interfaces.

Number of mimic diagrams for the entire CCMS is estimated to 88.

- archived data trends presentation or print,

- initiation of statistical reports generation and presentation,

- initiation of periodical reports generation and presentation or print,

- initiation of archived data export,

- presentation and print of alarm, event and action lists,

- authorisation and access control,

- number of user interfaces for:

    - issuing commands,

    - parameter change within predefined absolute limits,

    - acquisition parameter change,

    - system access,

    - administrative functions,

    - manual data entries,

if necessary access rights has been granted,

- basic data management support for valid historical data caching, which will speed up subsequent access and reduce the corporate WAN traffic.

- To install a printer available to all monitoring stations within the LAN,

- To expand the existing LAN to the new CCC2 premises, connecting of an additional monitoring station to the LAN,

- To dismantle the existing radio-communication, PLC and auxiliary equipment and to move it to a new location CCC3 Majdevo, in order to be reassembled there again.

The aforementioned equipment and labour will be sufficient for re-integration of CCC2 Direkcija into the new CCMS.

### 1.3.1.3	The CCC3 Majdevo

Present situation

The CCC3 Majdevo is at the moment a command and control centre for water treatment plant (WTP) Majdevo. The existing computational equipment within the CCC3 will remain within the scope of its present WTP monitoring and control functions and will not be included into the new CCMS,

The existing monitoring and control system was installed in 1995. It was conceptually supplement to the previously existing metering equipment. It was based on microprocessor controllers PC120, processing sensor signals directly, and on microprocessor acquisition devices MAP8, all connected into a network with PC computers, namely monitoring stations.

This network was RS485 based, had a bus topology and connected the microprocessor devices, a control room monitoring station, a Chief Technologist monitoring station, a General Manager monitoring station and Maintenance Department monitoring station. The network was also accessible via the public phone line by appropriate modems and interfaces.

All of the monitoring stations were equipped with software packages "MapNet", providing instantaneous insight into the plant measurements, historical trends presentation, data storage and statistical data processing and presentation.

The sample time was 10min. The system is operational and yet in use.

According to this design, new computational and communicational equipment will be installed on the premises of the existing WTP command and control centre, this forming the new command and control centre CCC3 for the regional water supply system. The CCC3 will provide:

- Monitoring the WTP Majdevo from the CCMS exclusively, with no possibilities of WTP control through the CCMS,

- Full monitoring and control from the CCC3 for the locations exclusively within the distribution networks DN Majdevo, DN Aleksandrovac and DN Nabrđe, since their initiating pump stations are located inside WTP. These distribution networks are not a part of the firs stage of CCMS realisation,

- Strict monitoring of all other locations in the regional water supply system from this CCC.

Equipment and labour required for CCC3 re-integration to the new CCMS

- In order to re-integrate CCC3 Majdevo into the CCMS, the following is required:

- To furbish the existing WTP control centre in order to establish a new command and control centre for the regional water supply system,

- To provide access from the CCC3 to logical WLL used by CCMS, which means:

- to provide data transfer over the network, using previously defined protocols,

- to install wireless Ethernet equipment and a router,

- to install over voltage and surge protection devices,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment,

- To expand the existing LAN in order to incorporate two additional monitoring stations and to integrate LAN to the WLL.

- To install two PC computers in the Technical manager's office and in the existing control room, which will be the new monitoring stations fitted for 24/7 operation, with a high resolution monitors 22", LAN support, a UPS systems and an over voltage/surge protectors,

- To install two SCADA packages compatible to the packages already running on stations within CCC2 Direkcija, in order to provide full visualisation of "The Regional System" on each new monitoring station in CCC3. In addition, SCADA packages must be configured to ensure operational control of distribution networks DN Majdevo, DN Aleksandrovac and DN Nabrđe. This will be achieved through:

- 15 appropriate mimic diagrams,

- historical trends,

- possibility of report generation and presentation,

- possibility of historical data export,

- alarm, event and action lists,

- basic data management support for valid historical data caching,

all of them concerning "The Regional System" and the three distribution networks, and also:

- access control and authorisation,

- possibility of issuing commands for the three considered distribution networks.

- To install a printer available to all monitoring stations within the LAN,

- To establish a radio-communication link between the local PLC-1.3 within the CCC3 Majdevo and the authorised communication centre PLC-4.2 in R Meševo 1.

- To reconstruct the existing control panel and command board, which means:

- connect the existing acquisition devices MAP8 to the PLC's communication module, via a RS485 fieldbus,

- connect signals concerning PS Majdevo, PS Aleksandrovac and PS Nabrđe directly to I/O modules of the PLC-1.3, in order to provide remote monitoring and control of these sites, which further means:

  - install three rotary 3-pole 1-0-2 switches for local-remote operation mode selection,

  - reconnect command circuitry in order to provide operation mode selection, remote control form ROMTK and signal monitoring to the ROMTK,

  - install auxiliary relays for contact multiplication,

  - install wire terminals for connecting with the ROMTK,

- install, label and connect signal cables between control panel/command board and ROMTK.

- To install a separate distribution cabinet ROMTK in CCC3 with the following:

- PLC-1.3 with a necessary communication module for mastering a local fieldbus with the acquisition devices MAP8, with over voltage communication line protection,

- radio-modem and over voltage power and communication line protections,

- all aforementioned WLL and LAN equipment, except for antenna systems,

- UPS system providing 8 hours autonomy,

- other auxiliary equipment.

Summary signal list, concerning signals that will be read by local fieldbus from the acquisition devices MAP8, is shown in the following table:

| MAP8 (current communication address “4”) |  |
| --- | --- |
| Measurement | Range |
| Raw water flow | 0 - 800 l/s |
| Flow total | 0 - 1580 l/s |
| Purified water flow | 0 - 800 l/s |
| Flow towards R Aleksandrovac | 0 - 800 l/s |
| Internal consumption flow | 0 - 60 l/s |
| Filter wash water flow | 0 - 800 l/s |
| Flow towards R Nabrđe | 0 - 5 l/s |
| Flow towards R Majdevo | 0 - 5 l/s |
| MAP8 (current communication address “5”) |  |
| Measurement | Range |
| Raw water turbidity | 0 - 30 NTU |
| Raw water chlorine residual | 0 - 1 mg/l |
| Raw water pH | 2 - 12 |
| Purified water turbidity | 0 - 1 NTU |
| Purified water chlorine residual | 0 - 2 mg/l |
| Purified water pH | 2 - 12 |
| Outdoor temperature | -40 ÷ +40 C |
| Water level in the WTP main storage reservoir | 0 - 5 m |
| MAP8 (current communication address “6”) |  |
| Measurement | Range |
| AC power, line “R” | 0 - 350 V |
| AC power, line “S” | 0 - 350 V |
| AC power, line “T” | 0 - 350 V |
| Ozone residual | 0 - 1 mg/l |
| WTP main storage overflow |  |
| Purified water flow towards R Bagdala,  1000 | 0 – 600 l/s |

- move the present Master PLC from CCC2 Direkcija into the ROMTK, where it will be assigned as PLC-1.3, and equip it with the application software which will:

  - perform regular data polls from acquisition devices MAP8, with polling time not longer than 30s, in order to retrieve the most recent measurements from MAP8 devices into the main storage area,

  - service data requests from the authorised command centre PLC-4.12 on the radio-modem network and send replies with the most recent data, including those retrieved from acquisition devices MAP8,

  - constantly performs self-diagnostic tests and places results in the main storage area.

- To upgrade the existing acquisition devices' software in order to provide data exchange with the PLC-1.3, using Modbus protocol and serial link via RS485.

The aforementioned equipment and labour will be sufficient for re-integration of CCC3 Majdevo into the new CCMS.

### 1.3.1.4	The CCC4 Bagdala

Present situation

The present command and control centre CCC4 Bagdala is located on the premises of the main town storage reservoir R Bagdala and the pumping station PS Bagdala. The centre was established in 2007, originally as the main command and control centre, but during the later CCMS expansions its function has been changed into a local command and control centre in charge of distribution network DN Šumice only. Nowadays, the monitoring and control of DN Šumice is possible from both CCC4 and CCC2. Such a configuration should be retained even in the new CCMS.

The CCC4 Bagdala is already equipped with radio-modem T96SR, PLC type CJ1M-CPU12 and one PC monitoring station with "MapNet" SCADA software package. At present times, monitoring of the main town storage reservoir R Bagdala is also possible in CCC4, as well as in CCC2. Details can be found in the as-built blueprints.

In the new CCMS the CCC4 Bagdala will retain its present functionality, i.e. the scope of monitoring and control functions it already has in the existing CCMS.

Equipment and labour required for CCC4 re-integration to the new CCMS

CCC4 Bagdala is already integrated into the existing CCMS. In order to adapt it for the new CCMS, the following is required:

- Link the existing monitoring station into the WLL using a router, instead of being connected directly to the serial communication port of PLC-1.7, as it is now,

- Reconfigure the existing SCADA package in order to obtain required data from the main server, instead directly from PLC-1.7, as it is the case now. The monitoring station should retain possibility of monitoring and control of DN Šumice.

The equipment and labour necessary to install WLL, as well as for functional upgrade of PLC-1.7, are listed in detail in a later chapter of this document, concerning R Bagdala within "The Regional System". These equipment and labour, along with the aforementioned, will be sufficient for re-integration of CCC4 Bagdala into the new CCMS.

### 1.3.1.5	The CCC5 Ćelije

Present situation

Artificial lake and dam Ćelije has already got a centralised monitoring and control system, covering the following objects: water intake, outlet valve house, upstream metering station in a village Ravni, downstream metering station in the village Suvaja and an administrative building.

The water intake construction is equipped with the following measurement devices:

- Flow meter, installed on the water mains  2600 mm,

- Storage level sensor,

- Water temperature sensors.

Flow metering on the mains  2600 mm is done by electromagnetic flow meter installed on a bypass pipeline  100 mm. Sensor signal is processed in a transmitter PC120F, displayed locally and transmitted remotely as current signal 0-20mA, ranging 0-74 m3/s.

Water storage level is measured by level transducer PC120H, while the signal is used also for operation of butterfly valves at elevations 280.00 m a.s.l., 277.00 m a.s.l., 274.00 m a.s.l., 271.00 m a.s.l., 268.00 m a.s.l. and 265.00 m a.s.l.

Water temperature is determined by means of Pt500 sensors and PRET04 converters in six depths, nearby water intakes. Temperature readings are converted into normalized current signals 0-20mA, corresponding to the ranges 0 0-40 °C, and sent to the administrative building by cables.

In the outlet valve-house, the following measurements are available:

- Flow metering through three pipes (CEV1, CEV2 and biological minimum duct)

- Main gate valve position.

The flow metering is done by Venturi tube flow meter, which is converting pressure difference into the flow rate signal. The current analogous 0-20mA is taken by cables into the administrative building.

The main gate position is determined by 10-turn 300 Ohm potentiometer, coupled with the gate valve mechanism turning 7 times from fully opened to fully closed valve position. The valve position is converted into current signal 0-1mA and sent by a cable into the administrative building.

A precipitation meter is installed on the roof of the administrative building.

The command and control centre CCC5 is located in the same building, equipped initially with a control panel and three microprocessor acquisition devices MAP8. During the CCMS reconstruction in 2006, a PLC controller CJ1M-CPU11 was installed for the integration of digital statuses and connected directly to the existing monitoring station. The monitoring station was equipped with "MapNet+" SCADA package, processing the signals from the PLC and three acquisition devices MAP8.

The software allows direct insight into instantaneous measurements, as well as historical data, which are archived locally in the integrated database. Report generation and statistical data processing are also available.

The existing CCC5 Ćelije is operating locally on the dam and artificial lake Ćelije and is not integrated into the existing CCMS in the public communal company JKP Vodovod. The list of signals monitored currently in the CCC5 is shown in the following table.

| MAP8 (current communication address “1”) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Channel |  | Measurement | Range | Unit |
| 1 |  | Water temperature at 277 m a.s.l. | 0 - 40 | °C |
| 2 |  | Water temperature at 274 m a.s.l. | 0 - 40 | °C |
| 3 |  | Water temperature at 271 m a.s.l. | 0 - 40 | °C |
| 4 |  | Water temperature at 268 m a.s.l. | 0 - 40 | °C |
| 5 |  | Water temperature at 265 m a.s.l. | 0 - 40 | °C |
| 6 |  | Water temperature at 255 m a.s.l. | 0 - 40 | °C |
| 7 |  | Not used |  |  |
| 8 |  | Not used |  |  |
| MAP8 (current communication address “2”) |  |  |  |  |
| Channel |  | Measurement | Range | Unit |
| 1 |  | Water storage level | 266.5 - 282.6 | m a.s.l. |
| 2 |  | Rasina river level in village Ravni | 0 – 200 | m |
| 3 |  | Rasina river inflow in Ravni | 0 - 71 | m3/s |
| 4 |  | Rasina river outflow in Suvaja | 0 - 89 | m3/s |
| 5 |  | Water mains flow rate | 0 - 74 | m3/s |
| 6 |  | Flow through pipe CEV I | 0 - 5 | m3/s |
| 7 |  | Flow through pipe CEV II | 0 - 5 | m3/s |
| 8 |  | Flow through pipe biological minimum pipe | 0 - 5 | m3/s |
| MAP8 (current communication address “3”) |  |  |  |  |
| Channel |  | Measurement | Range | Unit |
| 1 |  | Rasina river level in village Suvaja | 0 – 200 | cm |
| 2 |  | Precipitation amount on the dam | 0 - 10 | mm/h |
| 3 |  | Precipitation amount 10 km upstream | 0 - 10 | mm/h |
| 4 |  | Biological minimum valve position | 0 – 100 | % |
| 5 |  | CEV I valve position | 0 – 100 | % |
| 6 |  | CEV II valve position | 0 – 100 | % |
| 7 |  | Main gate valve position | 0 – 100 | % |
| 8 |  | Not used |  |  |
| PLC (current communication address "4") |  |  |  |  |
| No | Signal |  | Signal source |  |
| 01 | Opened water intake Z1 at 280 m a.s.l. |  | Water intake structure |  |
| 02 | Closed water intake Z1 at 280 m a.s.l. |  | Water intake structure |  |
| 03 | Opened water intake Z3 at 274 m a.s.l. |  | Water intake structure |  |
| 04 | Closed water intake Z3 at 274 m a.s.l. |  | Water intake structure |  |
| 05 | Opened water intake Z5 at 268 m a.s.l. |  | Water intake structure |  |
| 06 | Closed water intake Z5 at 268 m a.s.l. |  | Water intake structure |  |
| 07 | Opened water intake Z8 at 255 m a.s.l. |  | Water intake structure |  |
| 08 | Closed water intake Z8 at 255 m a.s.l. |  | Water intake structure |  |
| 09 | Opened water intake for tunnel flooding |  | Water intake structure |  |
| 10 | Closed water intake for tunnel flooding |  | Water intake structure |  |
| 11 | Opened water intake Z2 at 277 m a.s.l. |  | Water intake structure |  |
| 12 | Closed water intake Z2 at 277 m a.s.l. |  | Water intake structure |  |
| 13 | Opened water intake Z4 at 271 m a.s.l. |  | Water intake structure |  |
| 14 | Closed water intake Z4 at 271 m a.s.l. |  | Water intake structure |  |
| 15 | Opened water intake Z9 at 280 m a.s.l. |  | Water intake structure |  |
| 16 | Closed water intake Z9 at 280 m a.s.l. |  | Water intake structure |  |
| 17 | Opened water intake Z6 at 265 m a.s.l. |  | Water intake structure |  |
| 18 | Closed water intake Z6 at 265 m a.s.l. |  | Water intake structure |  |
| 19 | Opened water intake Z7 at 255 m a.s.l. |  | Water intake structure |  |
| 20 | Closed water intake Z7 at 255 m a.s.l. |  | Water intake structure |  |
| 21 | Hydraulic pump 1 running |  | Water intake structure |  |
| 22 | Hydraulic pump 2 running |  | Water intake structure |  |
| 23 | Hydraulic pump 1 failure |  | Water intake structure |  |
| 24 | Hydraulic pump 2 failure |  | Water intake structure |  |
| 25 | Hydraulic installation - high pressure |  | Water intake structure |  |
| 26 | Hydraulic installation - low pressure |  | Water intake structure |  |
| 27 | Drainage pump running |  | Water intake structure |  |
| 28 | Tower flooding |  | Water intake structure |  |
| 29 | Open door detector |  | Water intake structure |  |
| 30 | Transformer T1, Buchholz relay trip |  | Water intake structure |  |
| 31 | Transformer T1, emergency shut off |  | Water intake structure |  |
| 32 | Transformer T2 Buchholz relay trip |  | Water intake structure |  |
| 33 | Transformer T2, emergency shut off |  | Water intake structure |  |
| 33 | Hydraulic pump 3 running |  | Outlet valve house |  |
| 34 | Hydraulic pump 4 running |  | Outlet valve house |  |
| 35 | Hydraulic pump 3 bimetal thermostat trip |  | Outlet valve house |  |
| 36 | Hydraulic pump 4 bimetal thermostat trip |  | Outlet valve house |  |
| 37 | Hydraulic installation - high pressure |  | Outlet valve house |  |
| 38 | High pressure during the main gate valve closure |  | Outlet valve house |  |
| 39 | Manhole CEV1, 2 - Drainage pump running |  | Outlet valve house |  |
| 40 | Manhole BM - Drainage pump running |  | Outlet valve house |  |
| 41 | Drinking water pump running |  | Outlet valve house |  |
| 42 | Main gate valve opened |  | Outlet valve house |  |
| 43 | Main gate valve closed |  | Outlet valve house |  |
| 44 | Auxiliary gate valve opened |  | Outlet valve house |  |
| 45 | Auxiliary gate valve closed |  | Outlet valve house |  |
| 46 | Open door detector |  | Outlet valve house |  |
| 47 | AC power available |  | Control panel |  |

Equipment and labour required for CCC5 integration to the new CCMS

In order to integrate CCC5 Ćelije into the CCMS, the following is required:

- To furbish the existing control centre in order to establish a new command and control centre for the regional water supply system,

- To provide access from the CCC5 to logical WLL used by CCMS, which means:

- to provide data transfer over the network, using previously defined protocols,

- to install wireless Ethernet equipment and a router,

- to install over voltage and surge protection devices,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment,

- To connect the existing monitoring station to the WLL,

- To re-configure the existing SCADA package in order to:

- ensure two-way (client/server) data transfer between the main server in CCC1 Lipovac and this monitoring station, periodically every 30s. Data sent to the main server will include all the available information in the existing monitoring system in the CCC5. Data got from the main server will include:

  - inlet and outlet flow rates for WTP Majdevo and the level measurement in the R Majdevo, along with limit level indications,

  - valve positions, inlet and outlet pressure measurements and flow rate for the MRS Lipovac, along with limit pressure indications and valve limit switches' indications,

  - level measurements in both chambers of the storage reservoir R Lipovac, along with limit level indications,

  - valve positions, inlet and outlet pressure measurements and flow rate for the MRS Kruševac, along with limit pressure indications and valve limit switches' indications,

  - valve positions, inlet and outlet pressure measurements and flow rate for the MRS Stalać, along with limit pressure indications and valve limit switches' indications,

  - level measurements in both chambers of the storage reservoir R Todorova kula, along with limit level indications,

  - valve positions, inlet and outlet pressure measurements and flow rate for the MRS Ćićevac, along with limit pressure indications and valve limit switches' indications,

  - level measurements in both chambers of the storage reservoir R Ćićevac, along with limit level indications,

  - valve positions, inlet and outlet pressure measurements and flow rate for the MRS Varvarin, along with limit pressure indications and valve limit switches' indications,

  - level measurements in both chambers of the storage reservoir R Varvarin, along with limit level indications,

- provide at most two additional mimic diagrams containing all aforementioned measurements and indications concerning "The Regional System", for monitoring purposes only.

The aforementioned equipment and labour will be sufficient for integration of CCC5 Ćelije into the new CCMS and also for incorporating the basic information form the regional water supply system into the existing monitoring system on the Ćelije dam.

## 1.3.2	The Metering And Regulation Stations

There are five metering and regulation stations within the regional water supply system:

- MRS Lipovac, fully functional and with the existing control and monitoring equipment,

- MRS Kruševac, in the design phase,

- MRS Stalać, in the design phase,

- MRS Varvarin, in the design phase,

- MRS Ćićevac, in the design phase.

### 1.3.2.1	The MRS Lipovac

Present situation

- MRS Lipovac has been built in the village of Lipovac, 15km downstream the water mains from WTP Majdevo. It consists of two hydraulic lines, DN350 and DN600 intended for alternating seasonal operation. Each line has a regulation valve with an electric motor actuator, valve position transducer and limit position switches. Each line has two additional manually operated isolation valves, mounted before and after the corresponding regulation valve. Each of isolation valves is equipped with limit position switches.

According to blueprints for storage reservoir R Lipovac, a system of manually operated shut-off valves will be added at outlet of MRS Lipovac in order to direct water flow stream into the reservoir R Lipovac rather than directly into the town of Kruševac and R Bagdala, as it is now the case. This will be considered normal mode of operation and the future CCMS is designed accordingly. However, during regular maintenance of R Lipovac or in an accidental situation, it will be possible to bypass reservoir R Lipovac and let the water form MRS Lipovac directly into the town.

Although MRS Lipovac was equipped with all the necessary equipment, it has never been integrated into the existing CCMS due to valve control cabinet, which has not been assembled in accordance with the original MRS electrical design and does not provide remote control possibilities.

When an attempt was made to integrate MRS Lipovac into the CCMS during 2004, the following was done:

- A flow meter and inlet and outlet pressure sensors were installed,

- A separate distribution cabinet with the CCMS equipment was installed. This cabinet contains the PLC-1.5 (CJ1M-CPU12), various measurement equipment and a UPS system. Controller was also programmed to support necessary acquisition, diagnostic, control and protective functions. The list of signals is shown in the following table.

| PLC-1.5 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC power supply presence | 3 |  |  |  |
| Limit switches of four isolating valves | 8 |  |  |  |
| Limit switches of two regulation valves | 4 |  |  |  |
| Regulation valve statuses | 6 |  |  |  |
| Pushbutton statuses | 8 |  |  |  |
| High pressure on the outlet | 1 |  |  |  |
| Valve actuator commands |  | 4 |  |  |
| Local indication |  | 4 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Flow meter |  |  | 1 |  |
| Regulation valve position |  |  | 2 |  |
| Total | 30 | 8 | 5 | 0 |

- The radio-modem T96SR and all necessary auxiliary equipment was installed,

- The installed PLC software provides:

- remote manual operation mode of the MRS Lipovac,

- remote automatic operation mode, using either flow control algorithm or outlet pressure control algorithm. The operation mode and control algorithm are selectable remotely, with bumpless control algorithm changeover,

- in all operating modes, regulation valve motion is interrupted by series of pauses, in order to avoid hydraulic hammering due to abrupt valve movements and undesirable turbidity increases due to stationary flow disruptions. This holds both for remote and local operation modes, as anticipated by original electric design. However, the valve control cabinet erroneously allows direct control of valve actuators by installed pushbuttons, instead via the PLC.

MRS parameter summary

| MRS Lipovac |  |
| --- | --- |
| Valve manufacturer | MIN Niš |
| Pipe diameter | DN600, DN350 |
| Flow meter range | 0-800 l/s |
| Pressure range | 0-10 bar |

Equipment and labour required for the MRS integration into the CCMS

MRS Lipovac is not integrated into the CCMS. In order to integrate previously installed equipment, the following is required:

- Reconstruction of the command object containing control, measurement and communication equipment, which means construction of a ceiling and a proper roof, external wall insulation and rendering, side walkways, lightning protection and earthing installation, interior and exterior lighting installation,

- A detailed revision of the valve control cabinet and bringing it into accordance with the original electrical design, which means:

- reconnect internal wirings in order to provide remote control of valve actuators by means of voltage-free contacts from the existing separate CCMS distribution cabinet,

- install auxiliary contacts, relays and clamps in order to provide necessary monitoring signals to the CCMS distribution cabinet,

- reconnect internal wirings so that even in local operation mode valve actuator is controlled via PLC-1.5, not directly by pushbuttons. Omitting to do so has at least once caused a significant turbidity increase due to improperly prolonged manual command to a valve actuator.

- Wiring between the existing CCMS distribution cabinet and the adapted valve control cabinet,

- Replacement of the existing UPS device in the CCMS distribution cabinet with a new one providing 8 hours autonomy,

- Replacement of PLC-1.5 power supply module with the new one operating at 24VDC input,

- Reprogramming of the installed PLC-1.5 in order to:

- eliminate the existing downstream pressure control algorithm in remote operation mode, since this algorithm would become inappropriate after construction of reservoir R Lipovac,

- incorporate necessary logic for the support of a downstream reservoir level control algorithm in remote automatic mode of operation,

- adapt bumpless transfer logic to support remote manual operation mode and all control algorithms in remote automatic operation mode,

- provide necessary communication functions,

- Adjustment of radio-modem frequency and establishment of communication link to the authorised communication centre HPR Mali Šiljegovac (PLC-3.8),

- Complete functional testing and commissioning.

The aforementioned adaptations will be sufficient for integration of MRS Lipovac into the new CCMS.

### 1.3.2.2	The MRS Kruševac

Present situation

Metering and regulation station MRS Kruševac will be located in village of Makrešane, downstream the water mains from the town of Kruševac. The MRS Kruševac is in the design phase.

According to the design documentation, the MRS will have two hydraulic lines, duty and standby, each equipped with a regulation valve, two manually operated isolating valves and a flow meter. Inlet and outlet pressure sensors will be also installed within the MRS. This MRS is intended for hydraulic parameter control aimed at town network protection from downstrem disturbances.

The existing blueprints do not consider aspects of MRS integration in any form of monitoring or control system.

MRS parameter summary

| MRS Kruševac* |  |
| --- | --- |
| Valve manufacturer | ---- |
| Pipe diameter | DN350 |
| Flow meter range | 0-300 l/s |
| Pressure range | 0-15 bar |

*data available form the design documentation

Equipment and labour required for the MRS integration into the CCMS

In order to integrate MRS Kruševac into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.9 in the MRS and the authorised communication centre in R Bagdala (PLC-1.7). Securing the reliable data transfer on the radio-modem network between the local PLC and the authorised command centre,

- Inlet and outlet pressure sensor installation, each having a range 0-15 bar,

- Two flow meters installation, one on each hydraulic line, DN350/PN10, 0-300l/s,

- Inlet and outlet limit pressure detectors installation,

- Valve chamber flooding detector installation,

- Open door detector installation,

- Providing AC power supply to the MRS,

- Supply, delivery, installation and commissioning of a main distribution cabinet GRO, in all as shown in diagram "Main distribution cabinet GRO for MRS - Typical connection diagram". This cabinet provides:

- AC mains distribution for the MRS,

- local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",

- pushbutton valve control in local operation mode,

- valve control in remote operation mode by means of external voltage-free contacts,

- all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker-MPCB)

- local indication of valve status and position,

- all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.

- AC interior lighting and distribution installation,

- Wiring and connecting regulation valve actuators, isolating valves' limit position switches and other measurement and indicator equipment to GRO and ROMTK distribution cabinets,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK  - Typical connection diagram for MRS". The cabinet contains:

- the controller PLC-1.9,

- parts of metering and indicator equipment, including flow meter and pressure transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-1.9 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| AC supply present in GRO | 2 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Two regulation valves' limit position switches | 4 |  |  |  |
| Four isolation valves' limit position switches | 8 |  |  |  |
| Actuator motor statuses (run/MPCB) | 4 |  |  |  |
| Valve actuator failures (torque switches, thermal protection) | 8 |  |  |  |
| Inlet and outlet limit pressure indications | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| Valve chamber flooding detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Open/Close commands to regulation valves |  | 4 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Flow measurements |  |  | 2 |  |
| Regulation valve position |  |  | 2 |  |
| Total | 39 | 4 | 6 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct regulation valve control in remote operation modes. In remote automatic operation mode, three remotely selectable control algorithms are available: inlet pressure control algorithm, outlet pressure control algorithm and flow control algorithm. Protective functions are active in all remote operation modes,

  - communication services to client data requests or command messages, coming from the authorised communication centre PLC-1.7,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for MRS Kruševac integration into the CCMS.

### 1.3.2.3	The MRS Stalać

Present situation

Metering and regulation station MRS Stalać, still in the design phase, will be located on the water mains upstream from the storage reservoir R Todorova kula, providing regular and steady water supply of the Stalać municipality.

According to the design documentation, the MRS will have two hydraulic lines, duty and standby, each equipped with a regulation valve, a flow meter and two manually operated isolating valves. Inlet and outlet pressure sensors will be also installed within the MRS. This MRS is intended for hydraulic parameter control aimed primarily at steady water supply to storage reservoir R Todorova kula.

The existing blueprints do not consider aspects of MRS integration in any form of monitoring or control system.

MRS parameter summary

| MRS Stalać* |  |
| --- | --- |
| Valve manufacturer | ---- |
| Pipe diameter | DN150 |
| Flow meter range | 0-75 l/s |
| Pressure range | 0-15 bar |

* data available form the design documentation

Equipment and labour required for the MRS integration into the CCMS

In order to integrate MRS Stalać into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.11 in the MRS and the authorised communication centre in PS Globare (PLC-5.23),

- Inlet and outlet pressure sensor installation, each having a range 0-15 bar,

- Two flow meters installation, one on each hydraulic line, DN150/PN10, 0-75l/s,

- Inlet and outlet limit pressure detectors installation,

- Valve chamber flooding detector installation,

- Open door detector installation,

- Providing AC power supply to the MRS,

- Supply, delivery, installation and commissioning of a main distribution cabinet GRO, in all as shown in diagram "Main distribution cabinet GRO for MRS - Typical connection diagram". This cabinet provides:

- AC mains distribution for the MRS,

- local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",

- pushbutton valve control in local operation mode,

- valve control in remote operation mode by means of external voltage-free contacts,

- all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker-MPCB)

- local indication of valve status and position,

- all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.

- AC interior lighting and distribution installation,

- Wiring and connecting regulation valve actuators, isolating valves' limit position switches and other measurement and indicator equipment to GRO and ROMTK distribution cabinets,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK  - Typical connection diagram for MRS". The cabinet contains:

- the controller PLC-1.11,

- parts of metering and indicator equipment, including flow meter and pressure transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-1.11 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| AC supply present in GRO | 2 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Two regulation valves' limit position switches | 4 |  |  |  |
| Four isolation valves' limit position switches | 8 |  |  |  |
| Actuator motor statuses (run/MPCB) | 4 |  |  |  |
| Valve actuator failures (torque switches, thermal protection) | 8 |  |  |  |
| Inlet and outlet limit pressure indications | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| Valve chamber flooding detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Open/Close commands to regulation valves |  | 4 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Flow measurements |  |  | 2 |  |
| Regulation valve position |  |  | 2 |  |
| Total | 39 | 4 | 6 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct regulation valve control in remote operation modes. In remote automatic operation mode, two remotely selectable control algorithms are available: flow control algorithm and downstream reservoir level control algorithm. Protective functions are active in all remote operation modes,

  - communication services to client data requests or command messages, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for MRS Stalać integration into the CCMS.

### 1.3.2.4	The MRS Varvarin

Present situation

Metering and regulation station MRS Varvarin, still in the design phase, will be located on the water mains upstream from the storage reservoir R Varvarin, providing regular and steady water supply of the Varvarin municipality.

According to the design documentation, the MRS will have two hydraulic lines, duty and standby, each equipped with a regulation valve, a flow meter and two manually operated isolating valves. Inlet and outlet pressure sensors will be also installed within the MRS. This MRS is intended for hydraulic parameter control aimed primarily at steady water supply to storage reservoir R Varvarin.

The existing blueprints do not consider aspects of MRS integration in any form of monitoring or control system.

MRS parameter summary

| MRS Varvarin* |  |
| --- | --- |
| Valve manufacturer | ---- |
| Pipe diameter | DN250 |
| Flow meter range | 0-200 l/s |
| Pressure range | 0-15 bar |

* data available form the design documentation

Equipment and labour required for the MRS integration into the CCMS

In order to integrate MRS Varvarin into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.12 in the MRS and the authorised communication centre in PS Globare (PLC-5.23),

- Inlet and outlet pressure sensor installation, each having a range 0-15 bar,

- Two flow meters installation, one on each hydraulic line, DN250/PN10, 0-200l/s,

- Inlet and outlet limit pressure detectors installation,

- Valve chamber flooding detector installation,

- Open door detector installation,

- Providing AC power supply to the MRS,

- Supply, delivery, installation and commissioning of a main distribution cabinet GRO, in all as shown in diagram "Main distribution cabinet GRO for MRS - Typical connection diagram". This cabinet provides:

- AC mains distribution for the MRS,

- local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",

- pushbutton valve control in local operation mode,

- valve control in remote operation mode by means of external voltage-free contacts,

- all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker-MPCB)

- local indication of valve status and position,

- all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.

- AC interior lighting and distribution installation,

- Wiring and connecting regulation valve actuators, isolating valves' limit position switches and other measurement and indicator equipment to GRO and ROMTK distribution cabinets,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK  - Typical connection diagram for MRS". The cabinet contains:

- the controller PLC-1.12,

- parts of metering and indicator equipment, including flow meter and pressure transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-1.12 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| AC supply present in GRO | 2 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Two regulation valves' limit position switches | 4 |  |  |  |
| Four isolation valves' limit position switches | 8 |  |  |  |
| Actuator motor statuses (run/MPCB) | 4 |  |  |  |
| Valve actuator failures (torque switches, thermal protection) | 8 |  |  |  |
| Inlet and outlet limit pressure indications | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| Valve chamber flooding detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Open/Close commands to regulation valves |  | 4 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Flow measurements |  |  | 2 |  |
| Regulation valve position |  |  | 2 |  |
| Total | 39 | 4 | 6 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct regulation valve control in remote operation modes. In remote automatic operation mode, two remotely selectable control algorithms are available: flow control algorithm and downstream reservoir level control algorithm. Protective functions are active in all remote operation modes,

  - communication services to client data requests or command messages, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for MRS Varvarin integration into the CCMS.

### 1.3.2.5	The MRS Ćićevac

Present situation

Metering and regulation station MRS Ćićevac, still in the design phase, will be located on the water mains upstream from the storage reservoir R Ćićevac, providing regular and steady water supply of the Ćićevac municipality.

According to the design documentation, the MRS will have two hydraulic lines, duty and standby, each equipped with a regulation valve, a flow meter and two manually operated isolating valves. Inlet and outlet pressure sensors will be also installed within the MRS. This MRS is intended for hydraulic parameter control aimed primarily at steady water supply to storage reservoir R Ćićevac.

The existing blueprints do not consider aspects of MRS integration in any form of monitoring or control system.

MRS parameter summary

| MRS Ćićevac* |  |
| --- | --- |
| Valve manufacturer | ---- |
| Pipe diameter | DN250 |
| Flow meter range | 0-200 l/s |
| Pressure range | 0-15 bar |

*data available form the design documentation

Equipment and labour required for the MRS integration into the CCMS

In order to integrate MRS Ćićevac into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.13 in the MRS and the authorised communication centre in PS Globare (PLC-5.23),

- Inlet and outlet pressure sensor installation, each having a range 0-15 bar,

- Two flow meters installation, one on each hydraulic line, DN250/PN10, 0-200l/s,

- Inlet and outlet limit pressure detectors installation,

- Valve chamber flooding detector installation,

- Open door detector installation,

- Providing AC power supply to the MRS,

- Supply, delivery, installation and commissioning of a main distribution cabinet GRO, in all as shown in diagram "Main distribution cabinet GRO for MRS - Typical connection diagram". This cabinet provides:

- AC mains distribution for the MRS,

- local or remote operation mode selection, by means of a rotary multi-pole multi-position switch 1-0-2 meaning "Local-0-Remote",

- pushbutton valve control in local operation mode,

- valve control in remote operation mode by means of external voltage-free contacts,

- all necessary actuator and valve protections (limit and torque switches, thermal protections, motor protection circuit breaker-MPCB)

- local indication of valve status and position,

- all necessary monitoring signals for the separate CCMS distribution cabinet (ROMTK), by means of auxiliary contacts, relays and wire terminals.

- AC interior lighting and distribution installation,

- Wiring and connecting regulation valve actuators, isolating valves' limit position switches and other measurement and indicator equipment to GRO and ROMTK distribution cabinets,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK  - Typical connection diagram for MRS". The cabinet contains:

- the controller PLC-1.13,

- parts of metering and indicator equipment, including flow meter and pressure transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-1.13 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| AC supply present in GRO | 2 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Two regulation valves' limit position switches | 4 |  |  |  |
| Four isolation valves' limit position switches | 8 |  |  |  |
| Actuator motor statuses (run/MPCB) | 4 |  |  |  |
| Valve actuator failures (torque switches, thermal protection) | 8 |  |  |  |
| Inlet and outlet limit pressure indications | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| Valve chamber flooding detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Open/Close commands to regulation valves |  | 4 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Flow measurements |  |  | 2 |  |
| Regulation valve position |  |  | 2 |  |
| Total | 39 | 4 | 6 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct regulation valve control in remote operation modes. In remote automatic operation mode, two remotely selectable control algorithms are available: flow control algorithm and downstream reservoir level control algorithm. Protective functions are active in all remote operation modes,

  - communication services to client data requests or command messages, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for MRS Ćičevac integration into the CCMS.

## 1.3.3	The Storage Reservoirs

Five storage reservoirs belong to "The Regional System" and all of them will be integrated into the CCMS in the first stage of its realisation.

- R Lipovac, designed, awaiting for the construction,

- R Bagdala, reservoir already integrated in the existing CCMS,

- R Todorova kula, in the design phase,

- R Varvarin, in the design phase,

- R Ćićevac, in the design phase.

### 1.3.3.1	The R Lipovac

Present situation

The design documentation for the storage reservoir R Lipovac has already been completed, and construction is expected to begin soon.

The water will be reaching reservoir R Lipovac from the water mains via MRS Lipovac. The system of manually operated shut-off valves will be added at outlet of MRS Lipovac in order to direct water flow stream either into the reservoir R Lipovac or directly into the town's distribution network, as it is now the case. The latter mode of operation will be used only exceptionally, during the regular maintenance of R Lipovac or in an accidental situation.

Once the reservoir R Lipovac is finished and put into operation, it will supply not only town's distribution network and reservoir R Bagdala, but also the reservoirs R Varvarin, R Todorova kula and R Stalać.

The existing design documents do not consider aspects of the reservoir integration in any form of monitoring or control system.

The reservoir parameter summary

| R Lipovac* |  |
| --- | --- |
| Floor elevation | 210 m a.s.l. |
| Overflow elevation | 215 m a.s.l. |
| Capacity | 5000 m3 + 5000 m3 |
| Communication cable | ---- |
| Operation level indicator | Conductive level probes |
| AC power supply | Anticipated |

*data available form the design documentation

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Lipovac into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.6 in the R Lipovac and the authorised communication centre in HPR Mali Šiljegovac (PLC-3.8),

- Installation of two level sensors, one in each storage chamber, range 0-5m,

- Installation of a residual chlorine analyzer at reservoir's outlet, range 0-1mg/l

- Installation of a set of level indicators for detecting operating and limit water levels,

- Installation of open door detectors,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- the controller PLC-1.6,

- parts of metering and indicator equipment, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-1.6 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| Operating level detectors | 2 |  |  |  |
| Limit level detectors | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Level measurement |  |  | 2 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Total | 12 | 0 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests coming from the authorised communication centre PLC-3.8,

  - diagnostic functions for measuring equipment and the PLC itself.

- The aforementioned equipment and labour will be sufficient for R Lipovac integration into the CCMS.

### 1.3.3.2	The R Bagdala

Present situation

- Reservoir R Bagdala is the only storage reservoir within town's distribution network. It is currently supplied from the WTP Majdevo via MRS Lipovac, through the water mains DN1000, total length of 20.415m. After the construction of reservoir R Lipovac, reservoir R Bagdala will be supplied gravitationally from the R Lipovac and will compensate for daily variations in water consumption.

The reservoir R Bagdala consists of two hydraulically connected reservoirs, the Old one and the New one. The overflow elevation of the Old reservoir (212.00m a.s.l.) is one meter lower than overflow elevation of the New reservoir (213.00m a.s.l.), thus making 20% of the New reservoir capacity useless. A manually operated regulating valve has been installed on the common water intake to prevent overflows. This valve is operated seasonally, according to the operator experience. Apart from this valve, there are additional isolating valves at the inlet and outlet of each of two reservoirs; they are normally opened, except during the regular reservoir maintenance.

Both reservoirs within the R Bagdala have AC power supply and are located on the same premises as a pumping station PS Bagdala and CCC4 Bagdala. All these objects were integrated into the existing CCMS in 2007. Apart from R Bagdala, PS Bagdala and CCC4 Bagdala, an elevated upstream reservoir R Šumice, supplied by PS Bagdala, was also integrated at the time. Details are available in the existing as-builts.

- The CCMS integration during 2007 included:

- Additional cabling between the Old reservoir and CCC4 Bagdala for signal transmission,

- Installation of level sensors in both the Old and the New reservoir,

- Installation of operating and limit level detectors in both reservoirs,

- Installation of open door detectors in both reservoirs,

- Installation of a separate CCMS distribution cabinet, within the CCC4 Bagdala, with all the necessary measurement, indicator and control equipment. The installed PLC-1.7 (CJ1M-CPU12) was programmed to perform required acquisition, control, communication and diagnostic functions. The list of signals concerning R Bagdala is shown in the following table.

| PLC-1.7 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| Operating level detectors | 2 |  |  |  |
| Limit level detectors | 4 |  |  |  |
| Open door detectors | 2 |  |  |  |
| Valve chamber flooding detectors | 2 |  |  |  |
| UPS statuses | 1 |  |  |  |
| Level measurements |  |  | 2 |  |
| Inlet pressure measurement |  |  | 1 |  |
| Inlet flow measurement |  |  | 1 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Total | 12 | 0 | 5 | 0 |

- Installation of radio-modem (T96SR) and providing the radio-communication link to the CCC2 Direkcija, currently the main command and control centre of the existing CCMS. The PLC-1.7 also serves as a "store & forward" relay for message transmission to remote locations in the distribution network DN Kapidžija-Tekije and reservoir R Šumice. The PLC-1.7 also controls pumping station PS Bagdala,

- Installation of a monitoring PC station, equipped with the SCADA package "MapNet+". This station is locally connected to PLC-1.7 by serial communication, thus enabling monitoring of R Bagdala and also monitoring and control of the distribution network DN Šumice.

The reservoir parameter summary

| R Bagdala | The Old reservoir | The New reservoir |
| --- | --- | --- |
| Floor elevation | 208.09m a.s.l. | 208.09m a.s.l. |
| Overflow elevation | 212.00m a.s.l. | 213.00m a.s.l. |
| Capacity | 2800 m3 | 6500 m3 |
| Communication cable | IyStY 4 10x2x0.8 | IyStY 4 10x2x0.8 |
| Operation level indicator | Conducting level probes |  |
| AC power supply | Available |  |

Equipment and labour required for the reservoir re-integration into the new CCMS

The reservoir R Bagdala has been already integrated into the existing CCMS. In order to re-integrate this location in the new CCMS, the following is required:

- To provide access from the R Bagdala to logical WLL used by CCMS. Apart form R Bagdala, the network will connect another three communication centres R Meševo 1, HPR Mali Šiljegovac and PS Globare and all five command and control centres. This further means:

- to provide data transfer over the network, using previously defined protocols,

- to install wireless Ethernet equipment and a router,

- to install over voltage protection devices,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment.

- To establish an Ethernet LAN within the CCC4 Bagdala, which will connect two hosts, PLC-1.7 and the existing monitoring station. This further means:

- to install an appropriate network switch,

- to do a necessary UTP wiring inside the CCC4 premise between the PLC-1.7 and the existing monitoring station,

- to install other passive network equipment,

- to interconnect this LAN to the WLL.

- To upgrade the PLC-1.7 with an Ethernet communication module with the socket TCP/IP support,

- To re-adjust radio-modem frequency of the existing radio-modem in accordance with the new communication functions of this location,

- Retaining all acquisition, control and diagnostic functions of the existing PLC-1.7 software, upgrade its communication functions so that the following is provided:

- regular polling of all the communication slaves in a radio-modem network controlled by PLC-1.7, at sample rate not slower than once every 30s,

- buffering the most recently obtained data from the slaves in a storage area, together with IO signals obtained directly through its own IO modules,

- sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL, after all of the slaves have been polled in each 30s communication cycle,

- sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request, maintaining data integrity,

- reception of command messages from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network. The command messages have higher priority than regular polls,

- sending an additional poll to the slave previously targeted by a command message in order to provide command execution status in the shortest time possible. These additional polls have higher priority than regular polls,

- sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.

- To re-configure the existing SCADA software so that the monitoring station in CCC4 Bagdala exchanges data packages and command messages directly with the main server, rather than with the PLC-1.7, as it is now the case. From the user's point of view, all monitoring and control functions of this station must be retained,

- To install a residual chlorine analyzer and connect its output signal 4-20mA (0-1mg/l) to provided wire terminals in the existing ROMTK distribution cabinet,

- To install a flow meter on the PS Bagdala outlet to storage reservoir R Šumice.

- The aforementioned equipment and labour will be sufficient for re-integration of R Bagdala into the new CCMS, while preserving present monitoring and control functionality.

### 1.3.3.3	The R Todorova kula

Present situation

The reservoir R Todorova kula is being designed right now. It is anticipated to be the main drinkable water storage facility for the municipality of Stalać. The water will be reaching reservoir R Todorova kula from the water mains via MRS Stalać.

The existing design documents do not consider aspects of the reservoir integration in any form of monitoring or control system.

The reservoir parameter summary

| R Todorova kula* |  |
| --- | --- |
| Floor elevation | 202 m a.s.l. |
| Overflow elevation | 206 m a.s.l. |
| Capacity | 400 m3 |
| Communication cable | Not anticipated |
| Operation level indicator | Conductive level probe |
| AC power supply | Anticipated |

*data available form the design documentation

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Todorova kula into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.14 in the R Todorova kula and the authorised communication centre in PS Globare (PLC-5.23),

- Installation of two level sensors, one in each storage chamber, range 0-4m,

- Installation of a residual chlorine analyzer at reservoir's outlet, range 0-1mg/l

- Installation of a set of level indicators for detecting operating and limit water levels,

- Installation of open door detectors,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- the controller PLC-1.14,

- parts of metering and indicator equipment, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-1.14 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| Operating level detectors | 2 |  |  |  |
| Limit level detectors | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Level measurement |  |  | 2 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Total | 12 | 0 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for R Todorova kula integration into the CCMS.

### 1.3.3.4	The R Varvarin

Present situation

The reservoir R Varvarin is being designed right now. It is anticipated to be the main drinkable water storage facility for the municipality of Varvarin and also to provide water supply for a several rural settlements of municipalities Paraćin and Ćuprija. The water will be reaching reservoir R Varvarin from the water mains via MRS Varvarin.

- The existing design documents do not consider aspects of the reservoir integration in any form of monitoring or control system.

The reservoir parameter summary

| R Varvarin* |  |
| --- | --- |
| Floor elevation | 192 m a.s.l. |
| Overflow elevation | 196 m a.s.l. |
| Capacity | 4000 m3 |
| Communication cable | Not anticipated |
| Operation level indicator | Conductive level probe |
| AC power supply | Anticipated |

*data available form the design documentation

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Varvarin into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.15 in the R Varvarin and the authorised communication centre in PS Globare (PLC-5.23),

- Installation of two level sensors, one in each storage chamber, range 0-4m,

- Installation of a residual chlorine analyzer at reservoir's outlet, range 0-1mg/l

- Installation of a set of level indicators for detecting operating and limit water levels,

- Installation of open door detectors,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- the controller PLC-1.15,

- parts of metering and indicator equipment, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet. The signal summary is shown in the following table:

| PLC-1.15 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| Operating level detectors | 2 |  |  |  |
| Limit level detectors | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Level measurement |  |  | 2 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Total | 12 | 0 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for R Varvarin integration into the CCMS.

### 1.3.3.5	The R Ćićevac

Present situation

The reservoir R Ćićevac is being designed right now. It is anticipated to be the main drinkable water storage facility for the municipality of Ćićevac. The water will be reaching reservoir R Ćićevac from the water mains via MRS Ćićevac.

The existing design documents do not consider aspects of the reservoir integration in any form of monitoring or control system.

The reservoir parameter summary

| R Ćićevac* |  |
| --- | --- |
| Floor elevation | 202 m a.s.l. |
| Overflow elevation | 206 m a.s.l. |
| Capacity | 400 m3 |
| Communication cable | Not anticipated |
| Operation level indicator | Conductive level probe |
| AC power supply | Anticipated |

*data available form the design documentation

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Ćićevac into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement,

- Providing radio-communication link between the PLC-1.16 in the R Ćićevac and the authorised communication centre in PS Globare (PLC-5.23),

- Installation of two level sensors, one in each storage chamber, range 0-4m,

- Installation of a residual chlorine analyzer at reservoir's outlet, range 0-1mg/l

- Installation of a set of level indicators for detecting operating and limit water levels,

- Installation of open door detectors,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- the controller PLC-1.16,

- parts of metering and indicator equipment, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-1.16 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| Operating level detectors | 2 |  |  |  |
| Limit level detectors | 4 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Level measurement |  |  | 2 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Total | 12 | 0 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for R Ćićevac integration into the CCMS.

## 1.3.4	 The Chlorination Station HS Lipovac

Present situation

Chlorination station HS Lipovac is being designed right now. Its future location will be on the pipeline supplying water to distribution networks DN Modrica and DN Trmčare. The station will operate autonomously, with an integrated water flow meter and a chlorine residual analyzer, according to legislation.

The existing design documents do not consider aspects of the station integration in any form of monitoring or control system.

Equipment and labour required for the station integration into the CCMS

In order to integrate HS Lipovac into the CCMS, the following is required:

- Providing conditions for controller, indicator and communication equipment placement,

- Providing radio-communication link between the PLC-1.17 in the HS Lipovac and the authorised communication centre in HPR Mali Šiljegovac (PLC-3.8),

- Installation of an inlet pressure sensor,

- Installation of open door detectors,

- Reconstruction of the main distribution cabinet, in order to provide power supply for the CCMS distribution cabinet, which means installation of an appropriate two-pole circuit breaker 220VAC, 10A and wire terminals.

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK containing:

- the controller PLC-1.17,

- parts of indicator equipment, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment.

- The PLC must be properly connected to all measuring, indicator and communication equipment.

The signal summary is shown in the following table:

| PLC-1.17 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply present in ROMTK | 1 |  |  |  |
| Room flooding detector | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Chlorination equipment power status | 2 |  |  |  |
| Chlorination equipment operating statuses | 4 |  |  |  |
| Chlorination equipment faults | 4 |  |  |  |
| Chlorinator commands |  | 3 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Flow metering |  |  | 1 |  |
| Chlorine dosage measurement |  |  | 1 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Chlorine dosage set point |  |  |  | 1 |
| Total | 17 | 3 | 4 | 1 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests and command messages coming from the authorised communication centre PLC-3.8,

  - transferring start/stop commands and chlorine dosage set point, obtained form the     authorized command and control centre, to autonomous chlorinator, if applicable,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for HS Lipovac integration into the CCMS.

# 1.4	The Subsystem " The System East"

## 1.4.1	The Distribution Network DN Gaglovo 2

The distribution network consists of:

- A pumping station PS Gaglovo 2, which is supplied gravitationally from the storage reservoir R Tekije 1, which is already integrated into the existing CCMS,

- A hydro press (booster) station and storage reservoir HPR Mali Šiljegovac. The storage reservoir R Mali Šiljegovac is supplied via PS Gaglovo2, while the hydro press plant is pumping water from the reservoir to elevated distribution zones.

### 1.4.1.1	The PS Gaglovo 2

Present situation

Pumping station PS Gaglovo 2 (sometimes referred to as Novo Selo) is equipped with two pumps, one duty and one standby, each 7.5kW. PS Gaglovo 2 is capable of working only in a local automatic mode, according to an operating level signal from upstream reservoir HPR Mali Šiljegovac. The control circuitry in the motor control cabinet provides duty- standby pump rotation in successive pump restarts.

A pressure switch - pressostat, mounted on the suction pipe, is a dry running protection device. Inlet and outlet pipes are both DN80. The PS Gaglovo 2 has not yet been integrated into the CCMS. A cable PP00 3x2,5 mm2, laid between the reservoir R Mali Šiljegovac and PS Gaglovo 2, is used for transmitting an operating level signal from the upstream reservoir to the pumping station.

The PS parameter summary

| PS Gaglovo 2 – Novo Selo |  |
| --- | --- |
| Pump manufacturer | Elektrokovina |
| Pump type | VCV 250/8T |
| No of pumps | 1 duty, 1 standby |
| Motor power | 7,5kW |
| Flow | 3,0-5,8 l/s |
| Pump head | 57-128 m |
| Pump speed | 2910 rpm |
| Dry running protection | Pressostat |
| PS floor elevation | 206 m a.s.l. |

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Gaglovo 2 into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement, which means construction of metal platform annex inside the PS, lengthen from the doorway along the right side wall, 1m wide and properly supported,

- Providing radio-communication link between the PLC-3.7 in the PS Gaglovo 2 and the authorised communication centre in HPR Mali Šiljegovac (PLC-3.8),

- Installation of inlet and outlet pressure sensors,

- Installation of an outlet flow meter,

- Installation of a machine room flooding detector,

- Installation of open door detectors,

- Reconstruction of an existing motor control cabinet ROP, which means:

- redesign and reconstruction of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,

- installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,

- installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for PS". The cabinet contains:

- one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,

- interface relays for both input and output digital signals,

- auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-3.7, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-3.7 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROP cabinet | 1 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Statuses of duty pump selection switches | 2 |  |  |  |
| Status of local operation mode selection switch | 2 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Statuses of motor protection circuit breakers | 2 |  |  |  |
| Statuses of motor fuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detector | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Outlet flow measurement |  |  | 1 |  |
| Total | 22 | 2 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-3.8,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for PS Gaglovo 2 integration into the CCMS.

### 1.4.1.2	The HPR Mali Šiljegovac

Present situation

Hydro press and storage reservoir HPR Mali Šiljegovac is equipped with two duty pumps, each 4kW. One of the pumps has direct on line (DOL) starter, while the other is controller by a frequency inverter. The entire plant was intended for local automatic operation mode, maintaining the outlet pressure.

However, the installed local PLC (ZEN 10C1DR-D-V1) is not functioning properly and therefore only DOL pump is running, according to a signal from an auxiliary outlet pressure switch (pressostat). Since the plant was originally designed to maintain outlet pressure by fine adjustment of a pump speed, only a small pressure tank was installed with mainly protective function. This situation, along with erroneous local automatics, results in a frequent switching of a single pump.

Water is supplied to hydro booster from its own storage reservoir R Mali Šiljegovac. An outlet pressure sensor/transducer 0-10bar/4-20mA was installed for the purpose of fine outlet pressure control, along with an auxiliary pressure switch for accidental situations. At the moment, this pressostat is in control of the DOL pump. A level detector in the suction reservoir R Mali Šiljegovac provides dry running protection.

HPR Mali Šiljegovac has not yet been integrated into the CCMS. The installed motor control cabinet was not intended for such integration, let alone the local PLC, which has neither sufficient IO capacity nor communication capabilities for that.

The HPR parameter summary

| HP Mali Šiljegovac |  |
| --- | --- |
| Pump manufacturer | BBC Elettropompe |
| Pump type | T100B2 |
| No of pumps | 2 duty |
| Motor power | 4 kW |
| Flow | 3-8 l/s |
| Pump head | 40-52 m |
| Pump speed | 2840 rpm |
| Dry running protection | Float level switch |
| HP floor elevation | 330 m a.s.l. |
| No of tanks | 1 |
| Tank capacity | 10 l |
| Maximum pressure | 10 bar |
| R Mali Šiljegovac |  |
| Floor elevation | 320 m a.s.l. |
| Overflow elevation | 323 m a.s.l. |
| Capacity | 150 m3 |
| Communication cable | --- |
| Operation level indicator | Float level switch |
| AC power supply | Provided |

Equipment and labour required for the HPR integration into the CCMS

In order to integrate HPR Mali Šiljegovac into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of metal platform annex inside the HPR, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported,

- To establish a communication centre and belonging radio-modem network by installing the necessary radio-communication equipment,

- To provide access to the logical WLL used by CCMS, connecting all four communication centres and all five command and control centres, which means:

- to provide data transfer from the location, using previously defined protocols,

- to install wireless Ethernet equipment,

- to install over voltage and surge protectors,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment.

- To install a new outlet pressure sensor,

- To install a storage level sensor with appropriate over voltage protectors,

- To install an outlet limit pressure detector,

- To install a machine room flooding detector,

- To install storage level indicators for detecting operating and limit water levels,

- To install chlorine residual analyzer,

- To install open door detectors,

- To reconstruct the existing motor control cabinet ROP, which means

- installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,

- installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for HPR". The cabinet contains:

- parts of metering and indicator equipment, especially transducers, display units etc.

- protective and interfacing devices for analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-3.8, with a communication module for radio-modem network and an Ethernet communication module with the socket TCP/IP support. The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-3.8 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply statuses in the ROP cabinet | 2 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Pump motor faults | 2 |  |  |  |
| Outlet operating pressure switch status | 1 |  |  |  |
| Outlet limit pressure switch statuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Frequency inverter fault reset |  | 1 |  |  |
| Storage level measurement |  |  | 1 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Frequency inverter reference setting |  |  |  | 1 |
| Total | 22 | 3 | 4 | 1 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - diagnostic functions for measuring equipment and the PLC itself,

  - a set of communication functions:

  - regular polling of all the communication slaves in a radio-modem network controlled by PLC-3.8, at sample rate not slower than once every 30s,

  - buffering the most recently obtained data from the slaves in a storage area, together with IO signals obtained directly through its own IO modules,

  - sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL, after all of the slaves have been polled in each 30s communication cycle,

  - sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request, maintaining data integrity,

  - reception of command messages from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network. The command messages have higher priority than regular polls,

  - sending an additional poll to the slave previously targeted by a command message in order to provide command execution status in the shortest time possible. These additional polls have higher priority than regular polls,

  - sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.

The aforementioned equipment and labour will be sufficient for HPR Mali Šiljegovac integration into the CCMS.

# 1.5	The Subsystem “The Rasina Wally System”

## 1.5.1	The Distribution Network Naupare

- This distribution network consists of:

- Pumping station PS Naupare 1, supplied directly from the water mains from WTP Majdevo,

- Storage reservoir R Naupare 1, supplied from the pumping station PS Naupare 1,

- Pumping station PS Naupare 2, supplied from the distribution pipeline connecting PS Naupare 1 and R Naupare 1,

- Storage reservoir R Naupare 2, supplied from the pumping station PS Naupare 2.

### 1.5.1.1	The PS Naupare 1

Present situation

The pumping station PS Naupare 1 is equipped with two pumps, one duty and one standby unit. The pumping station is designed to operate either in local manual or local automatic operation mode. According to the design, the selected pump is activated autonomously in the local automatic operation mode, depending on an upstream reservoir level detector signal. A pressure switch, mounted on the suction pipe, is a dry running protection device.

However, this pumping station became incapable of local automatic operation, when the cable transferring upstream level signal was severely damaged. Since the cable was beyond repair, a temporary ad hoc solution was made in 2007, by substituting damaged cable with an SMS messaging system using GSM technology.

During this intervention, command circuitry of only one pump was modified so that instead of upstream level detector contact, an output relay contact of GSM device was used. On the other hand, the GSM device was configured to activate or deactivate the output relay upon reception of an SMS from the compatible GSM device in the upstream reservoir R Naupare 1. The GSM device and necessary auxiliary equipment was placed into a separate distribution cabinet.

- Additionally, a bimetal thermostat protector signal concerning the chosen motor was also introduced into the GSM device. Upon the activation of the signal, GSM device would send a warning message to previously configured phone numbers. This GSM based control system operates solely between PS Naupare 1 and R Naupare 1 and is neither a part of the existing CCMS nor any other monitoring system.

The PS parameter summary

| PS Naupare 1 |  |
| --- | --- |
| Pump manufacturer | Elektrokovina |
| Pump type | ---- |
| No of pumps | 1+1 |
| Motor power | ---- |
| Flow | ---- |
| Pump head | 58-62 m |
| Pump speed | ---- |
| Dry running protection | Pressostat |
| PS floor elevation | 209 m a.s.l. |

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Naupare 1 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of metal platform annex inside the PS, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported,

- To provide radio-communication link between the PLC-4.20 in the PS Naupare 1 and the authorised communication centre in R Meševo 1 (PLC-4.12),

- To provide relay support to the WLL used by CCMS, which means:

- providing backhaul support for the WLL,

- to install wireless Ethernet equipment and necessary active network equipment,

- to install over voltage and surge protectors,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment.

- To install inlet and outlet pressure sensors,

- To install an outlet flow meter,

- To install a machine room flooding detector,

- To install an open door detector,

- To dismantle the existing control cabinet with the GSM device,

- To reconstruct the existing motor control cabinet ROP, which means:

- removal of the GSM device output relay contact from a motor control circuitry,

- installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- installation of two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,

- auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes,

- redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,

- installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,

- installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for PS". The cabinet contains:

- interface relays for both input and output digital signals,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.20, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.20 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROP cabinet | 1 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Statuses of duty pump selection switches | 2 |  |  |  |
| Status of local operation mode selection switch | 0 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Statuses of motor protection circuit breakers | 2 |  |  |  |
| Statuses of motor fuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detector | 0 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Outlet flow measurement |  |  | 1 |  |
| Total | 19 | 2 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for PS Naupare 1 integration into the CCMS.

### 1.5.1.2	The R Naupare 1

Present situation

Storage reservoir R Naupare 1 is supplied form the PS Naupare 1. The storage facility has AC power supply. The existing cable to PS Naupare 1 has been badly damaged, so that storage operating level signal is transferred to PS Naupare 1 by means of an SMS reporter exploiting GSM technology. The GSM device in the storage facility generates a SMS each time when storage level triggers a level detector. The compatible GSM device in the downstream pumping station PS Naupare 1 receives the message and activates or deactivates one pump accordingly, by means of an output relay contact, incorporated into the pump motor command circuitry. This way the damaged cable is substituted by a GSM based control system, providing local automatic operation mode of PS Naupare 1 and R Naupare 1.

The storage reservoir R Naupare 1 has not been integrated into the CCMS, and installed GSM system operates only locally for these two objects. The GSM equipment is mounted in a separate distribution cabinet.

The reservoir parameter summary

| R Naupare 1 |  |
| --- | --- |
| Floor elevation | 264 m a.s.l. |
| Overflow elevation | 270 m a.s.l. |
| Capacity | 150 m3 |
| Communication cable | PP00 3 x 2,5 mm2, broken |
| Operation level indicator | Conductive level probes |
| AC power supply | Available |

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Naupare 1 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement,

- To provide a proper AC power supply in the storage facility,

- To provide radio-communication link between the PLC-4.21 in the R Naupare 1 and the authorised communication centre in R Meševo 1 (PLC-4.12),

- To install a storage level sensor,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- To dismantle and remove the existing GSM device and its wiring,

- To reconstruct the main distribution cabinet RO, in order to provide power supply for the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.21, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.21 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Total | 9 | 0 | 1 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests, coming from the authorised communication centre PLC-4.12,

  - diagnostic functions for measuring equipment and the PLC itself.

- The aforementioned equipment and labour will be sufficient for R Naupare 1 integration into the CCMS.

### 1.5.1.3	The PS Naupare 2

Present situation

The pumping station PS Naupare 2 is supplied with water form the distribution pipeline connecting PS Naupare 1 and R Naupare 1. It is equipped with two pumps, one duty and one standby. Like PS Naupare 1, this pumping station was also designed for local manual or local automatic operation mode, the latter based on a level detector signal from the upstream reservoir R Naupare 2. A dry running protection is provided by a suction pipe pressostat.

Although the pumping station has been recently constructed and put into operation, the cable connecting it to the upstream reservoir has been broken, preventing the operating level signal from reaching the motor control cabinet in the PS Naupare 2. Therefore, this pumping station cannot operate in local automatic mode.

So far, the PS Naupare 2 was integrated neither into the CCMS, nor in a local GSM based control system operating between PS Naupare 1 and R Naupare 1.

The PS parameter summary

| PS Naupare 2 |  |
| --- | --- |
| Pump manufacturer | Elektrokovina |
| Pump type |  |
| No of pumps | 1+1 |
| Motor power |  |
| Flow |  |
| Pump head | 65-68 m |
| Pump speed |  |
| Dry running protection | Pressostat |
| PS floor elevation | 251 m a.s.l. |

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Naupare 2 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of metal platform annex inside the PS, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported,

- To provide radio-communication link between the PLC-4.22 in the PS Naupare 2 and the authorised communication centre in R Meševo 1 (PLC-4.12),

- To install inlet and outlet pressure sensors,

- To install an outlet flow meter,

- To install a machine room flooding detector,

- To install an open door detector,

- To reconstruct the existing motor control cabinet ROP, which means:

- installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- installation of two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,

- auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes,

- redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,

- installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,

- installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for PS". The cabinet contains:

- interface relays for both input and output digital signals,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.22, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.22 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROP cabinet | 1 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Statuses of duty pump selection switches | 2 |  |  |  |
| Status of local operation mode selection switch | 2 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Statuses of motor protection circuit breakers | 2 |  |  |  |
| Statuses of motor fuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detector | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Outlet flow measurement |  |  | 1 |  |
| Total | 22 | 2 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,

  - diagnostic functions for measuring equipment and the PLC itself.

- The aforementioned equipment and labour will be sufficient for PS Naupare 2 integration into the CCMS.

### 1.5.1.4	The R Naupare 2

Present situation

The reservoir R Naupare 2 is supplied with water from the downstream pumping station PS Naupare 2. This storage facility has no AC power supply, and there is no power distribution network in the vicinity of the storage premises.

The existing cable between R Naupare 1 and the downstream PS Naupare 1 has been broken, preventing local automatic operation of PS Naupare 2. As a result, storage reservoir R Naupare 2 experiences unsteady water supply.

The R Naupare 2 has been integrated neither into the CCMS, nor in a local GSM based control system operating between PS Naupare 1 and R Naupare 1.

The reservoir parameter summary

| R Naupare 2 |  |
| --- | --- |
| Floor elevation | 312 m a.s.l. |
| Overflow elevation | 315 m a.s.l. |
| Capacity | 120 m3 |
| Communication cable | PP00 3 x 2,5 mm2, broken |
| Operation level indicator | Float level switch |
| AC power supply | Unavailable |

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Naupare 2 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement,

- To provide AC power supply in the storage facility,

- To provide radio-communication link between the PLC-4.23 in the R Naupare 2 and the authorised communication centre in R Meševo 1 (PLC-4.12),

- To install a storage level sensor,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- To reconstruct the main distribution cabinet RO, in order to provide power supply for the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.23, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.23 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Total | 9 | 0 | 1 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests, coming from the authorised communication centre PLC-4.12,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for R Naupare 2 integration into the CCMS.

## 1.5.2	The Distribution Network Šogolj-Meševo

The distribution network Šogolj-Meševo consists of:

- The pumping station PS Šogolj, gravitationally supplied with water from the water mains connected directly to WTP Majdevo,

- The storage reservoir R Meševo 1 supplied from the pumping station PS Šogolj, intended for water provision of a village Doljane,

- The storage reservoir R Meševo 2, supplied gravitationally from the reservoir R Meševo 1,

- The hydro press (booster) HP Cerova, supplied gravitationally from the reservoir R Meševo 2, pumping water into elevated consumer areas.

### 1.5.2.1	The PS Šogolj

Present situation

The pumping station PS Šogolj is equipped with one duty and one standby pump, each rated 10kW. The pumping station is designed for operation in a local automatic mode only, depending on the upstream reservoir level. Motor command circuitry provides duty-standby pump rotation.

There is no dry running protection on the suction pipe. Inlet and outlet pipes are both DN100. A cable PP00-Y 3x2.5 mm2 connects PS Šogolj and the upstream reservoir R Meševo 1, transferring a water level signal used for pump control. The pumping station PS is not integrated into the CCMS.

The PS parameter summary

| PS Šogolj |  |
| --- | --- |
| Pump manufacturer | Elektrokovina |
| Pump type | VCV 250/10T |
| No of pumps | 1+1 |
| Motor power | 10kW |
| Flow | 3,0-5,8 l/s |
| Pump head | 72-154 m |
| Pump speed | 2850 rpm |
| Dry running protection | None |
| PS floor elevation | 210 m a.s.l. |

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Šogolj into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of metal platform annex inside the PS, lengthen to the right from doorway, along the front wall to the right side wall, 1m wide and properly supported,

- To provide radio-communication link between the PLC-4.11 in the PS Šogolj1 and the authorised communication centre in R Meševo 1 (PLC-4.12),

- To install inlet and outlet pressure sensors,

- To install an outlet flow meter,

- To install a machine room flooding detector,

- To install a inlet pressure switch (pressostat) for dry running protection,

- To install an open door detector,

- Reconstruction of an existing motor control cabinet ROP, which means:

- redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,

- installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,

- installation of auxiliary contacts, relays and clamps in order to connect the motor control cabinet to the CCMS cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for PS". The cabinet contains:

- one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,

- interface relays for both input and output digital signals,

- auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.11, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.11 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROP cabinet | 1 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Statuses of duty pump selection switches | 2 |  |  |  |
| Status of local operation mode selection switch | 2 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Statuses of motor protection circuit breakers | 2 |  |  |  |
| Statuses of motor fuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detector | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Outlet flow measurement |  |  | 1 |  |
| Total | 22 | 2 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for PS Šogolj integration into the CCMS.

### 1.5.2.2	The R Meševo 1

Present situation

The storage reservoir R Meševo 1 (Doljane) is supplied from the downstream pumping station PS Šogolj. The cable has been laid in order to transfer float level switch signal form the reservoir to the PS Šogolj, where it is used for pump operation in local automatic mode.

AC power supply is not available in the facility. Furthermore, the existing cable has insufficient capacity for power supply.

This reservoir has not been integrated into the CCMS.

The reservoir parameter summary

| R Meševo 1 |  |
| --- | --- |
| Floor elevation | 302 m a.s.l. |
| Overflow elevation | 305 m a.s.l. |
| Capacity | 180 m3 |
| Communication cable | PP00 3 x 2,5 mm2 |
| Operation level indicator | Float level switch |
| AC power supply | Unavailable |

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Meševo 1 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of an additional room, leant on the front wall, to the left of storage doorway, with a separate entrance,

- To provide AC power supply in the storage facility,

- To establish a communication centre and belonging radio-modem network by installing the necessary radio-communication equipment,

- To provide access to the logical WLL used by CCMS, connecting all four communication centres and all five command and control centres, which means:

- to provide data transfer from the location, using previously defined protocols,

- to install wireless Ethernet equipment,

- to install over voltage and surge protectors,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment.

- To install a storage level sensor,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- To reconstruct the main distribution cabinet, in order to provide power supply for the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors; an appropriate communication centre aerial system will be mounted outdoors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.12, with both a communication module for radio-modem network support and an Ethernet communication module with the socket TCP/IP support. The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.12 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Total | 9 | 0 | 1 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - diagnostic functions for measuring equipment and the PLC itself,

  - a set of communication functions:

  - regular polling of all the communication slaves in a radio-modem network controlled by PLC-4.12, at sample rate not slower than once every 30s,

  - buffering the most recently obtained data from the slaves in a storage area, together with IO signals obtained directly through its own IO modules,

  - sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL, after all of the slaves have been polled in each 30s communication cycle,

  - sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request, maintaining data integrity,

  - reception of command messages from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network. The command messages have higher priority than regular polls,

  - sending an additional poll to the slave previously targeted by a command message in order to provide command execution status in the shortest time possible. These additional polls have higher priority than regular polls,

  - sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.

The aforementioned equipment and labour will be sufficient for R Meševo 1 integration into the CCMS.

### 1.5.2.3	The R Meševo 2

Present situation

The storage reservoir R Meševo 2 is supplied gravitationally from the reservoir R Meševo 1. AC power supply is not available in the facility. There is no inlet regulating valve intended for water level control.

An AC power distribution network is in the vicinity of storage premises, approx. 50m away. This reservoir has not been integrated into the CCMS.

The reservoir parameter summary

| R Meševo 2 |  |
| --- | --- |
| Floor elevation | 262 m a.s.l. |
| Overflow elevation | 265 m a.s.l. |
| Capacity | 120 m3 |
| Communication cable | --- |
| Operation level indicator | --- |
| AC power supply | 0.4kV power network in vicinity |

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Meševo 2 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of an additional room, leant on the front wall, to the left of storage doorway, with a separate entrance,

- To provide AC power supply in the storage facility,

- To provide radio-communication link between the PLC-4.13 in the R Meševo 2 and the authorised communication centre in R Meševo 1 (PLC-4.12),

- To install a storage level sensor,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- To reconstruct the main distribution cabinet, in order to provide power supply for the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.13, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.13 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Total | 9 | 0 | 1 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests, coming from the authorised communication centre PLC-4.12,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for R Meševo 2 integration into the CCMS.

### 1.5.2.4	The HP Cerova

Present situation

The hydro booster HP Cerova is supplied gravitationally from the storage reservoir R Meševo 2. Its operation is essential for water supply to elevated distribution zones.

The HP Cerova is originally designed with two duty and one standby pump, each 2.7kW. Two pressure tanks were mounted, each capacity of 25l. The facility was intended for local automatic operation, keeping the outlet pressure within predefined limits.

However, the facility has been looted and therefore out of function, with only two remaining pumps, with no motor control cabinet and broken dry protection pressure switch. Traces of frequent machine room flooding are also visible.

The HP Cerova has not been integrated into the CCMS. There are not cables or communication links of any kind to any other object within the regional water supply system.

The HP parameter summary

| HP Cerova |  |
| --- | --- |
| Pump manufacturer | Elektrokovina |
| Pump type | VCV 100/4S |
| No of pumps | 2 duty, 1 standby |
| Motor power | 2.7 kW |
| Flow | 1.2-2.2 l/s |
| Pump head | 27-57 m |
| Pump speed | 2840 rpm |
| Dry running protection | Pressostat |
| HP floor elevation | 260 m a.s.l. |
| No of tanks | 2 |
| Tank capacity | 25 l |
| Maximum pressure | 8 bar |

Equipment and labour required for the HP integration into the CCMS

- In order to integrate HP Cerova into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of metal platform annex inside the HP, lengthen to the left from doorway, along the front wall to the left side wall, 1m wide and properly supported,

- To provide radio-communication link between the PLC-4.14 in the HP Cerova and the authorised communication centre in R Meševo 1 (PLC-4.12),

- To install inlet and outlet pressure sensors,

- To install an outlet limit pressure detector,

- To replace the existing inlet pressostat for dry running protection with a new one,

- To install a machine room flooding detector,

- To install open door detectors,

- Supply, delivery, installation and commissioning of a new motor control cabinet ROP, which will contain:

- a main switch and an appropriate main circuit breaker,

- one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- three sets, each containing:

  - a DOL starter with auxiliary contacts for local and remote signalisation,

  - a three-pole circuit breaker with either auxiliary contacts or AC line monitor, status contacts intended for command logic and signalling.

  - appropriate bimetal thermostat protection with auxiliary contacts for command circuitry and signalling;

- command circuitry of the following characteristics

  - possibility of two duty pumps operation according to two outlet pressostats' signals, but only in local automatic mode,

  - possibility of duty-standby rotation changeover on every HP shutdown, but only in local automatic mode,

  - possibility of pump control from the CCMS distribution cabinet ROMTK in remote operation modes, with no interference of duty rotation logic or outlet pressostat signals,

  - bimetal thermostat protection, circuit breaker protection and dry running protection must be incorporated regardless of operation mode.

- auxiliary contacts and relays for remote signalling of dry running protection status, outlet pressostats' signals, AC power supply status and motor statuses,

- local fault indicators,

- necessary clamps for interconnection with the equipment and the CCMS distribution cabinet;

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for HP". The cabinet contains:

- parts of metering and indicator equipment, especially transducers, display units etc.

- protective and interfacing devices for analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-4.14, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-4.14 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply statuses in the ROP cabinet | 2 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Pump motor running statuses | 3 |  |  |  |
| Statuses of motor protection circuit breakers | 3 |  |  |  |
| Statuses of motor circuit breakers | 3 |  |  |  |
| Outlet operating pressure switch statuses | 2 |  |  |  |
| Outlet limit pressure switch statuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 3 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Total | 25 | 3 | 2 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-4.12,

  - diagnostic functions for measuring equipment and the PLC itself,

The aforementioned equipment and labour will be sufficient for HP Cerova integration into the CCMS.

# 1.6	The Subsystem "The Morava System”

## 1.6.1	The Distribution Network Srnje

- The distribution network Srnje comprises total of eight locations:

- The pumping station PS Srnje 1, supplied directly from the town distribution network,

- The storage reservoir R Srnje 1, supplied with water from downstream pumping station PS Srnje 1. The pumping station PS Krvavica-Padež is located within the same facility, pumping water from R Srnje 1 into two upstream storage reservoirs, both part of this distribution network:

    - the first group of pumps is supplying an upstream reservoir R Krvavica,

    - the second group of pumps is supplying an upstream reservoir R Padež,

- The pumping station PS Globare, gravitationally supplied from the storage reservoir R Krvavica,

- The storage reservoir R Globare, supplied from the downstream pumping station PS Globare,

- The pumping station PS Srnje 2, gravitationally supplied from the storage reservoir R Srnje 1,

- The storage reservoir R Srnje 2, supplied from the downstream pumping station PS Srnje 2.

### 1.6.1.1	The PS Srnje 1

Present situation

The pumping station PS Srnje 1 (Kruševica) is equipped with two duty pumps, each rated 15kW. The station can operate either in local manual or local automatic mode, while the mode is selectable for each pump separately, by means of two switches on the motor control cabinet. In local automatic mode, pumps are controlled by level signals from the upstream storage reservoir R Srnje 1.

The pump is supplied with water directly from the distribution network. A pressostat on the suction pipe provides dry running protection.

Between the PS Srnje 1 and upstream reservoir R Srnje 1 a cable PP00 3x2.5 mm2 is laid, transferring operating level signals. For the time being, PS Srnje 1 is not integrated into the CCMS.

The PS parameter summary

| PS Srnje 1 |  |
| --- | --- |
| Pump manufacturer | Jastrebac |
| Pump type | NVP 50-4 |
| No of pumps | 2 |
| Motor power | 15kW |
| Flow | 8,0-9,0 l/s |
| Pump head | 80-75 m |
| Pump speed | 2910 rpm |
| Dry running protection | Pressostat |
| PS floor elevation | 170 m a.s.l. |

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Srnje 1 into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement, which means construction of an additional dedicated room alongside the PS,

- Providing radio-communication link between the PLC-5.17 in the PS Srnje 1 and the authorised communication centre in PS Globare (PLC-5.23),

- Installation of inlet and outlet pressure sensors,

- Installation of an outlet flow meter,

- Installation of a machine room flooding detector,

- Installation of open door detectors,

- Reconstruction of an existing motor control cabinet ROP, which means:

- installation of one new rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- upgrading of existing rotary switches with additional poles in order to provide selection signalisation into the CCMS,

- redesign of motor command circuitry, which means:

  - to reconnect wirings in order to provide both remote and local motor control,

  - to redefine the function of existing rotary switches in order to provide duty pump selection and appropriate signalisation into the CCMS,

  - to bypass upstream reservoir operating level signals when in remote operation mode,

- either replacement of plug fuses with circuit breakers or installation of additional AC line monitors after the fuses, in both cases with auxiliary contacts for command circuitry integration and signalisation into the CCMS,

- installation of auxiliary contacts, relays and wire terminals in order to provide all required monitoring signals to the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for PS". The cabinet contains:

- interface relays for both input and output digital signals,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.17, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.17 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROP cabinet | 1 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Statuses of duty pump selection switches | 2 |  |  |  |
| Status of local operation mode selection switch | 2 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Statuses of motor protection circuit breakers | 2 |  |  |  |
| Statuses of motor circuit breakers /AC line monitors | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detector | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Outlet flow measurement |  |  | 1 |  |
| Total | 22 | 2 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for PS Srnje 1 integration into the CCMS.

### 1.6.1.2	The PS Krvavica-Padež and R Srnje 1

Present situation

The pumping station PS Krvavica-Padež is equipped with two groups of pumps, one for water supply to storage reservoir R Krvavica and another to reservoir R Padež. Hydraulically, each pump group can be treated as a separate pumping facility with it own distribution network.

Both pump groups are supplied from the common suction reservoir R Srnje 1, located on the same premises, capacity 500m3. Dry running protection is provided by a level detector in the suction reservoir. Common intake pipe has a diameter DN100, while the outlet pipes for the directions Krvavica and Padež are DN200 and DN100, respectively.

The pump group for direction Krvavica consists of two duty pumps, each rated 7.5kW. These pumps can operate only in local automatic mode, depending on level signals form the upstream reservoir R Krvavica. The group has its own motor control cabinet.

The pump group for direction R Padež consists also of two duty pumps, each 4kW. Each pump in the group can operate either in local manual or local automatic mode, depending on two selection switches on a separate motor control cabinet. Automatic pump operation is governed by level signals from the upstream reservoir R Padež.

Two separate signal cables has been laid, one from PS Krvavica-Padež to R Krvavica and another from PS Krvavica-Padež to R Padež, both for level signal transfer. Unfortunately, the cable to R Krvavica has been broken and pumps for this reservoir are operated manually, thanks to an improvisation in command circuitry.

In the motor control cabinet ROP for direction Padež, a controller (ZEN type) was already installed. However, it has insufficient IO, communication and expanding capabilities for integration into the CCMS.

The pumping station PS Krvavica-Padež has not been integrated into the CCMS yet.

The PSR parameter summary

| PS Krvavica-Padež |  |  |
| --- | --- | --- |
|  | Krvavica | Padež |
| Pump manufacturer | Elektrokovina | BBC Elettropompe |
| Pump type | VCV 250/7 T | T100B2 IEC60034 |
| No of pumps | 1+1 | 1+1 |
| Motor power | 7,5 kW | 4 kW |
| Flow | 3,0-5,8 l/s | ---- |
| Pump head | 50-112 m | ---- |
| Pump speed | 2910 rpm | 2840 rpm |
| Dry running protection | Conducting level probes |  |
| PS floor elevation | 258 m a.s.l. | 258 m a.s.l. |
| R Srnje 1 |  |  |
| Floor elevation | 257 m a.s.l. |  |
| Overflow elevation | ---- |  |
| Capacity | 500 m3 |  |
| Communication cable | PP00-Y 3x1.5 |  |
| Operation level indicator | Conducting level probes |  |
| AC power supply | Available |  |

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Krvavica-Padež and R Srnje 1 into the CCMS, the following is required:

- Providing conditions for control, measurement and communication equipment placement, which means construction of metal platform annex inside the PS, lengthen to the right from doorway, along the font wall to the right side wall, 1m wide and properly supported,

- Providing radio-communication link between the PLC-5.18 in the PS Krvavica-Padež and the authorised communication centre in PS Globare (PLC-5.23),

- Installation of two pressure sensors at the outlets of both pump groups,

- Installation of two flow meters at the outlets of both pump groups,

- Installation of a storage level sensor,

- Installation of operating and limit level detectors in the storage reservoir,

- Installation of a machine room flooding detector,

- Installation of open door detectors,

- Reconstruction of an existing motor control cabinet for the pumps supplying R Padež:

- redesign motor command circuitry:

  - eliminate the existing micro-PLC and reconnect wirings in order to provide both remote and local motor control,

  - redefine the function of existing rotary switches in order to provide duty pump selection and appropriate signalisation into the CCMS,

  - bypass upstream reservoir operating level signals when in remote operation mode,

- installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,

- installation of auxiliary contacts, relays and wire terminals in order to provide necessary monitoring signals to the CCMS cabinet,

- Reconstruction of an existing motor control cabinet for the pumps supplying R Krvavica:

- redesign motor command circuitry in order to provide both remote and local motor control,

- installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,

- installation of auxiliary contacts, relays and wire terminals in order to provide necessary monitoring signals to the CCMS cabinet,

- Supply, delivery, installation and commissioning of one CCMS distribution cabinet ROMTK, according to diagram "Distribution cabinet ROMTK - Typical connection diagram for PSR". The cabinet contains:

- two rotary multi-pole 3-position switches 1-0-2 intended for local or remote operation mode selection, one for each group of pumps,

- two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode, both for the pumps supplying R Krvavica,

- interface relays for both input and output digital signals, for both pump groups,

- auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes, for both pump groups,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals for both pump groups,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.18, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.18 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply statuses in the ROP cabinet | 2 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 4 |  |  |  |
| Statuses of duty pump selection switches | 4 |  |  |  |
| Statuses of local operation mode selection switch | 4 |  |  |  |
| Pump motor running statuses | 4 |  |  |  |
| Statuses of motor protection circuit breakers | 4 |  |  |  |
| Statuses of motor fuses | 4 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detectors | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 4 |  |  |
| Inlet pressure measurement |  |  | 2 |  |
| Outlet pressure measurement |  |  | 2 |  |
| Storage level measurement |  |  | 1 |  |
| Total | 36 | 4 | 5 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre, for both pump groups,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for PS Krvavica-Padež and R Srnje 1 integration into the CCMS.

### 1.6.1.3	The R Krvavica

Present situation

The storage reservoir R Krvavica is supplied from the pumping station PS Krvavica-Padež. There is no AC power supply in the object, while the recently laid signal cable has already been broken. This cable was intended for level signal transfer to the downstream pumping station PS Krvavica-Padež, where the signal would have been used for local automatic pump operation.

The R Krvavica has not been integrated neither the CCMS.

The reservoir parameter summary

| R Krvavica |  |
| --- | --- |
| Floor elevation | 307 m a.s.l. |
| Overflow elevation | ---- |
| Capacity | 250 m3 |
| Communication cable | PP00 3 x 2,5 mm2 |
| Operation level indicator | Float level switch |
| AC power supply | Unavailable |

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Krvavica into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement,

- To provide AC power supply in the storage facility,

- To provide radio-communication link between the PLC-5.21 in the R Krvavica and the authorised communication centre in PS Globare (PLC-5.23),

- To provide relay support to the WLL used by CCMS, which means:

- providing backhaul support for the WLL,

- to install wireless Ethernet equipment and necessary active network equipment,

- to install over voltage and surge protectors,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment.

- To install a storage level sensor,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- To reconstruct the main distribution cabinet, in order to provide power supply for the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.21, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.21 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Total | 9 | 0 | 1 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

- The aforementioned equipment and labour will be sufficient for R Krvavica integration into the CCMS.

### 1.6.1.4	The R Padež

Present situation

The storage reservoir R Padež is supplied from the pumping station PS Krvavica-Padež. There is no AC power supply in the object. A signal cable has been laid between this object and the downstream pumping station. This cable provides level signals transfer to the PS Krvavica-Padež, where the signal is utilised for local automatic pump operation.

The R Padež has not been integrated into the CCMS. The existing signal cable is inappropriate for AC power transmission. The nearest power distribution line is about 600m away.

The reservoir parameter summary

| R Padež |  |
| --- | --- |
| Floor elevation | 253 m a.s.l. |
| Overflow elevation | ---- |
| Capacity | ---- |
| Communication cable | PP00 3 x 2,5 mm2 |
| Operation level indicator | Float level switch |
| AC power supply | Unavailable |

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Padež into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement,

- To provide AC power supply in the storage facility,

- To provide radio-communication link between the PLC-5.22 in the R Padež and the authorised communication centre in PS Globare (PLC-5.23),

- To install a storage level sensor,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- To reconstruct the main distribution cabinet, in order to provide power supply for the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.22, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.22 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Total | 9 | 0 | 1 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

- The aforementioned equipment and labour will be sufficient for R Padež integration into the CCMS.

### 1.6.1.5	The PS Globare

Present situation

- At the moment, this pumping station is in its design stage. Its future location has been determined, while its construction has not yet begun.

Based on the design documentation available so far and on experience with the similar facilities in the regional water supply system, it can be expected that the PC Globare will be equipped with two pumps, capable of both local manual and local automatic operation mode. Automated pump operation will be governed by an upstream reservoir level signal.

- The pumping station will be supplied with water gravitationally, from the storage reservoir R Krvavica. A pressostat will be mounted on a suction pipe to provide dry running protection. A signal cable is anticipated from the pumping station to the upstream reservoir R Globare for level signal transmission.

- The design documentation available so far did not anticipate PS Globare integration in the existing CCMS.

The PS parameter summary

| PS Globare* |  |
| --- | --- |
| Pump manufacturer | ---- |
| Pump type | ---- |
| No of pumps | 1+1 |
| Motor power | ---- kW |
| Flow | ---- l/s |
| Pump head | ---- m |
| Pump speed | ---- rpm |
| Dry running protection | Pressostat |
| PS floor elevation | ---- m a.s.l. |

*data available form the design documentation

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Globare into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement,

- To establish a communication centre and belonging radio-modem network by installing the necessary radio-communication equipment,

- To provide access to the logical WLL used by CCMS, connecting all four communication centres and all five command and control centres, which means:

- to provide data transfer from the location, using previously defined protocols,

- to install wireless Ethernet equipment,

- to install over voltage and surge protectors,

- to install UPS system providing 8 hours autonomy,

- to install other auxiliary equipment.

- To install inlet and outlet pressure sensors,

- To install an outlet flow meter,

- To install a machine room flooding detector,

- To install an open door detector,

- To reconstruct the existing motor control cabinet ROP, which means:

- redesign of motor command circuitry in order to provide additional remote motor control capability and signalisation to the CCMS,

- installation of AC line monitors after the fuses for each motor and integration into the motor command circuitry,

- installation of auxiliary contacts, relays and wire terminals in order to provide necessary monitoring signals to the CCMS cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for PS". The cabinet contains:

- one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,

- interface relays for both input and output digital signals,

- auxiliary relays for motor command circuitry reconstruction, providing normal PS operation both in previously existing local or recently introduced remote modes,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.23, with a communication module for radio-modem network and an Ethernet communication module with the socket TCP/IP support. The PLC must be properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.23 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROP cabinet | 1 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Statuses of duty pump selection switches | 2 |  |  |  |
| Status of local operation mode selection switch | 2 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Statuses of motor protection circuit breakers | 2 |  |  |  |
| Statuses of motor fuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detector | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Outlet flow measurement |  |  | 1 |  |
| Total | 22 | 2 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - diagnostic functions for measuring equipment and the PLC itself,

  - a set of communication functions:

  - regular polling of all the communication slaves in a radio-modem network controlled by PLC-5.23, at sample rate not slower than once every 30s,

  - buffering the most recently obtained data from the slaves in a storage area, together with IO signals obtained directly through its own IO modules,

  - sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL, after all of the slaves have been polled in each 30s communication cycle,

  - sending a message containing the most recent data from all the devices on the radio-modem network to the Master PLC-1.1 over WLL on its specific request, maintaining data integrity,

  - reception of command messages from the Master PLC-1.1 over WLL and their routing to the targeted PLC through radio-modem network. The command messages have higher priority than regular polls,

  - sending an additional poll to the slave previously targeted by a command message in order to provide command execution status in the shortest time possible. These additional polls have higher priority than regular polls,

  - sending the most recent command execution status, from the slave previously targeted by a command message, to the Master PLC-1.1 over WLL.

The aforementioned equipment and labour will be sufficient for PS Globare integration into the CCMS.

### 1.6.1.6	The R Globare

Present situation

At the moment, this storage facility is in its design stage. So far, the location of the reservoir is known, while its construction has not yet begun.

The reservoir R Globare will be supplied with water from the downstream pumping station PS Globare. There is no power distribution network in the vicinity of the storage location. Also, the existing design documentation did not anticipate AC power supply on the premises. However, a signal cable will be laid to the downstream pumping station in order to provide level signal transfer and automated pump operation.

- Remote monitoring or control issues of the R Globare are not considered in the existing design documents.

The reservoir parameter summary

| R Globare* |  |
| --- | --- |
| Floor elevation | ---- m a.s.l. |
| Overflow elevation | ---- m a.s.l. |
| Capacity | 120 m3 |
| Communication cable | ---- |
| Operation level indicator | Float level switch |
| AC power supply | Not anticipated |

*data available form the design documentation

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Globare into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement,

- To provide AC power supply in the storage facility,

- To provide radio-communication link between the PLC-5.24 in the R Globare and the authorised communication centre in PS Globare (PLC-5.23),

- To install a storage level sensor,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.24, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.24 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Total | 9 | 0 | 1 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

- The aforementioned equipment and labour will be sufficient for R Globare integration into the CCMS.

### 1.6.1.7	The PS Srnje 2

Present situation

The pumping station PS Srnje 2 is equipped with two duty pumps, each rated 4kW. The facility can operate solely in local automatic mode, depending on a level signal in the upstream storage reservoir R Srnje 2.

The pumping station is supplied with water gravitationally, from the reservoir R Srnje 1. A pressure switch (pressostat) installed on the suction pipe protects pumps from dry running. Both inlet and outlet pipes have diameter 2.5".

- A signal cable, running from the pumping station to the upstream reservoir R Srnje 2, transfers level signals. The cable type is PP00 3x2,5 mm2.

- The pumping station PS Srnje 2 has not yet been integrated into the CCMS. The existing company's voice radio communications do not operate properly on the premises.

The PS parameter summary

| PS Srnje 2 |  |
| --- | --- |
| Pump manufacturer | Elektrokovina |
| Pump type | VCV 100 8T |
| No of pumps | 2 |
| Motor power | 4kW |
| Flow | 1,2-2,2 l/s |
| Pump head | 61-120 m |
| Pump speed | 2670 rpm |
| Dry running protection | Pressostat |
| PS floor elevation | 225 m a.s.l. |

Equipment and labour required for the PS integration into the CCMS

In order to integrate PS Srnje 2 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement, which means construction of an additional room leant on the existing object, with a separate entrance,

- To provide radio-communication link between the PLC-5.19 in the PS Srnje 2 and the authorised communication centre in PS Globare (PLC-5.23),

- To install inlet and outlet pressure sensors,

- To install an outlet flow meter,

- To install a machine room flooding detector,

- To install an open door detector,

- To reconstruct the existing motor control cabinet ROP, which means:

- installation of one rotary multi-pole 3-position switch 1-0-2 intended for local or remote operation mode selection,

- installation of two rotary multi-pole 3-position switches 1-0-2 intended both for duty pump selection in remote mode or manual/remote selection in local operation mode,

- redesign of motor command circuitry:

  - reconnect wirings in order to provide both remote and local motor control,

  - either replace the existing motor fuses with appropriate circuit breakers with auxiliary contacts, or install AC line monitors after the fuses for each motor, and integrate power status signal into the circuitry,

  - integrate rotary switches for duty pump selection and provide appropriate signalisation into the CCMS,

  - bypass upstream reservoir operating level signals when in remote operation mode;

- installation of auxiliary contacts, relays and wire terminals in order to provide necessary monitoring signals to the CCMS cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for PS". The cabinet contains:

- interface relays for both input and output digital signals,

- parts of metering and indicator equipment, especially flow meter transducer, display units etc.

- protective and interfacing devices for analogue signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.19, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.19 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROP cabinet | 1 |  |  |  |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| "Local-0-Remote" switch statuses | 2 |  |  |  |
| Statuses of duty pump selection switches | 2 |  |  |  |
| Status of local operation mode selection switch | 2 |  |  |  |
| Pump motor running statuses | 2 |  |  |  |
| Statuses of motor protection circuit breakers | 2 |  |  |  |
| Statuses of motor fuses | 2 |  |  |  |
| Dry running protection | 1 |  |  |  |
| Machine room flooding detector | 1 |  |  |  |
| Upstream reservoir operating level detector | 1 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Motor run commands |  | 2 |  |  |
| Inlet pressure measurement |  |  | 1 |  |
| Outlet pressure measurement |  |  | 1 |  |
| Outlet flow measurement |  |  | 1 |  |
| Total | 22 | 2 | 3 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - direct pump control in remote manual or remote automatic operation mode, according to commands and protective parameters obtained from the authorised centre,

  - continuous execution of protective procedures for the equipment and the water supply system,

  - communication services to client data requests and command messages, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

The aforementioned equipment and labour will be sufficient for PS Srnje 2 integration into the CCMS.

### 1.6.1.8	The R Srnje 2

Present situation

The storage reservoir R Srnje 2 is supplied from the pumping station PS Srnje 2. There is no AC power supply on the premises. A signal cable has been laid between this object and the downstream pumping station, transferring float level switch signal required for automated pump operation.

The R Srnje 2 has not been integrated into the CCMS. The existing signal cable is inappropriate for AC power transmission. The nearest power distribution line is about 400m away.

The reservoir parameter summary

| R Srnje 2 |  |
| --- | --- |
| Floor elevation | ---- |
| Overflow elevation | 300 m a.s.l. |
| Capacity | 60 m3 |
| Communication cable | PP00 3 x 2,5 mm2 |
| Operation level indicator | Float level switch |
| AC power supply | Unavailable |

Equipment and labour required for the reservoir integration into the CCMS

In order to integrate R Srnje 2 into the CCMS, the following is required:

- To provide conditions for control, measurement and communication equipment placement,

- To provide AC power supply in the storage facility,

- To provide radio-communication link between the PLC-5.20 in the R Srnje 2 and the authorised communication centre in PS Globare (PLC-5.23),

- To install a storage level sensor,

- To install a chlorine residual analyzer,

- To install storage level detectors for operating and limit water levels,

- To install an open door detector,

- To reconstruct the main distribution cabinet, in order to provide power supply for the CCMS distribution cabinet,

- Supply, delivery, installation and commissioning of the CCMS distribution cabinet ROMTK, in all as shown in diagram "Distribution cabinet ROMTK - Typical connection diagram for R". The cabinet contains:

- parts of metering and indicator equipment, transducers, display units etc.

- protective and interfacing devices for both analogue and digital signals,

- the radio-modem accompanied with power and communication line protectors,

- the UPS system with batteries, providing 8 hours autonomy,

- other auxiliary equipment,

- the controller PLC-5.20, properly connected to all measuring, indicator and communication equipment within the cabinet.

The signal summary is shown in the following table:

| PLC-5.20 signal description | DI | DO | AI | AO |
| --- | --- | --- | --- | --- |
| AC supply status in the ROMTK cabinet | 1 |  |  |  |
| Storage operating level detector | 1 |  |  |  |
| Storage limit level detector | 2 |  |  |  |
| Open door detector | 1 |  |  |  |
| UPS statuses | 4 |  |  |  |
| Storage level measurement |  |  | 1 |  |
| Chlorine residual measurement |  |  | 1 |  |
| Total | 9 | 0 | 2 | 0 |

- The PLC must be programmed in order to provide:

  - immediate acquisition of all signals connected to PLC's I/O modules,

  - communication services to client data requests, coming from the authorised communication centre PLC-5.23,

  - diagnostic functions for measuring equipment and the PLC itself.

- The aforementioned equipment and labour will be sufficient for R Srnje 2 integration into the CCMS.

Part 3: Transmission Main to Cicevac and Varvarin

A) TECHNICAL DESCRIPTION

1. PIPELINE MCB I – WT VARVARIN

Transmission pipeline is passing through village Maskare, and after to a long line through fields to the location of new built tank “Varvarin”.

At the point T54 it connects on the regional pipeline which is provided with water from the regional pipeline – accumulation “Celije”. The length of this section is 5356,72 m, and the diameter of the pipeline is DN 400. The point 135 is the connection point on the part of the pipe which leads water into the tank Varvarin.

The pipeline level follows the ground line. The minimal depth of the digging is defined on the basis of protected depth of the freezing and it is 1,3 m ( layer depth 0,8 m).

In the settlement, where the pipeline is passing through the streets, because of traffic load, the minimal depth is defined to 1,7 m.

On the crossing point with traffic arteries the digging depth is 2 m.

The pipeline is mostly passing through green ground (through fields) and when it passes through the settlement, the pipeline directs through green ground where ever that is possible.

On the pipeline parts, which passes under traffic arteries, the symmetrical cutting off is predicted, for traffic cover (asphalt or concrete), 20 cm wide than the width of the trench.

During the production of pipeline in the gas line zone, the digging must be handy done in the presence of authority of Gasification firm.

On the passing point under the road in the point 90, protective steel pipe 508/6,3 mm is built in by the impressing, the length of  L = 7,0 m and through it the polyethylene pipe insured with PVC or PE distancers is pulled through.

On the vertical line fractures underground air valves are placed and also over ground hydrant for washing out of the pipeline.

For the separation of some parts of the pipeline on the distance of 1 - 1,5 km the section covers are placed.

Euro covers of the short realization are predicted.

All metal frameworks are placed over ground with cast caps and built in shift.

1.1. Pipes

Selected pipe material is polyethylene of high density, quality class 100 (PE 100). Pipes are connected with frontal heat according to the manufacture intructions.

Pipeline is put in the excavation trench of the length 1,0 m on the sand cover thickness of 10 cm. After putting pipes covers with sand or with fine ground without sharp objects to 30 cm above the pipe top and sand stamps with handy ram of 10 kg. Pipe joints have to be uncovered until the pressure testing.

When the pipeline is tested on pressure, the trench is covered with soil from the excavation in 30 cm layers and stamp down with vibro boards, in the part of the line which passes through green ground.

On the line part, which passes through asphalt and macadam, all trench is covered with sand with stamping down with vibro boards and wetting. The rest 30 cm covers with gravel and makes the base for paving with asphalt.

At the end, the trench pave with asphalt and the street drives in the original state. At the work on macadam, the trench covers to 25 cm from the peak elevation of the ground, and then the macadam construction lays to the peak elevation of the ground.

Trench covering in traffics is predicted with sand because of faster settling.

After work, the pipe washes out and disinfect according to instruction given in general technical condition.

1.2. Section iron

Section irons are predicted of ductile casting. The way of putting and protection is the same as with cast stage pieces.

1.3. Fittings

1.3.1. Valves

1. Body valve constructions are without fillers for bearing of the gasket disk so it is not possible deposition in the filler.

2. Gasket disc is coated with rubber by which small rough spots are annulled on the bearing of the valves.

3. Gasket disc rein are teflon made, and it makes opening and closing of the valve easier.

4. Spindle valve gasket is done over variety rubber and Teflon valves, in regard to problems which don’t exist during the maintenance of “stop valve“.

1.3.2. Air valve

An air valve is protected with casting iron cap which is in the ground level, and the valve “head” is about 7 – 10 cm lower. But it must take care that casting iron cap do not fill with ground, in which case the air flow will be disabled. Air valve top must be free in the height of 15 cm.

1.3.3. Muddy drainpipe

Pipeline washing out is predicted by over ground hydrants. Muddy drainpipe construction is done at the way that each part of the pipeline can be washed out separate. On the muddy drainpipe points the section valve is placed by which the parts of the pipe – line can be isolated.

1.3.4. Flange adapters

On the occasion of choosing flange  adapters must take care about the type of material on which they are placed, also about outside diameter of the pipeline on which, they are also placed. On the occasion of choosing flange adapters we give an advantage over adapters which don’t have coil for screws in the metal framework body so they tighten with screws and nuts.

2. PIPELINE MRB II = WT CICEVAC

2.1. Introduction

Pipeline is worked out from the tank “Todor Tower” to the Cicevac tank (MRB II – Tank Cicevac). Defined polyethylene pipe diameter for supply of Cicevac is DN 400.

2.2. Pipeline PE DN 400 description

The pipeline beginning is the connection in the manhole which serve for division of the water line from Pojate to “Todor Tower” tank. The manhole is dimensioned it the way that it also serves for discharge of the pipeline on the part from the manhole to “Todor Tower” tank. With valves undisturbed work is regulated for both section in the case of the damage. Behind the manhole connection the flow measure manhole is predicted in which placing electromagnetic flow measures DN 350 is also predicted.

Pipeline DN 400 passing across fields and approaching asphalt road on the left in the Cicevac direction. On ST 1 + 097,27 muddy drainpipe manhole is projected which empty to the South Morava. On that section, pipeline goes up vertical to the lower bridge porter across the South Morava where it is fixed and on that way crosses the river. On that section in the length of 108 m pipe is covered with protective foil and isolate from freezing according to the rules. On the upper pipeline level the air valve is placed. On the other side of the bridge on ST 1 + 250, 96 muddy drainpipe is placed, drainage of water is also to the South Morava. That manhole also serves for pounding of the pipeline through levee. Crossing through levee is possible with impressing of steel pipeline DN 600 through which polyethylene pipeline DN 400 passes. On the other side of the levee is the manhole with valve. On ST 1 + 462, 99 air valve manhole is placed.

In extension, the pipeline goes behind buildings down the meadow. Following the configuration of the ground on ST 1 + 862, 82 muddy drainpipe is placed, on ST 2 + 192, 52 air valve and on ST 2 + 013, 69 muddy drainpipe. From that point pipeline approaches railway where it keeps going on properly distance of 10 m and more from the railway.

At the top 35 the manhole for pipeline impressing is projected because that is the point of crossing the pipeline under the railway. The pipe is impress to the top 36 in length of 27 m. The steel pipe DN 600 is impress through which polyethylene pipe DN 400 is passing. It is also the muddy drainpipe manhole, and on the other side of the railway is the manhole with valve. On ST 5 + 103, 34 there is the manhole for drainage and on ST 5 + 143, 19 the manhole for impressing of the pipeline. On this section the pipeline passes under main road Pojate – Krusevac. The impressing is done in the length of 38 m.

The pipeline goes to the Cicevac tank, mostly through fields.

The pipeline end is the enter and the connection with valve chamber in Cicevac.

New pipeline connection DN 350 is predicted in valve chamber in Cicevac which consist of two chambers. Existing pipe installation in tank Cicevac are:

- water line to tank chamber LG DN 200 on which the flat valve DN 200 is placed

- drainpipe LG DN 100 on which the flat valve DN 100 is placed

- overflowing pipe DN 200 on which the drainpipe is connected.

Projected quantity of water which transports through polyethylene pipeline DN 400 to tank is 42 L/S and from that reason connecting new and existing pipeline is predicted in the tank covering. It is predicted that polyethylene pipeline DN 400 (inner diameter DN 354, 2) keeps going down the steel water pipe DN 350 in tank covering so the pipeline can be installed by welding because of specific condition of installation. On the pipeline, installation of the flat bolt DN 200 NP 10 is predicted. For connecting of the pipeline changing of existing FF piece DN 200 with T piece DN 200 is predicted.

2.3. Objects on the pipeline

On the pipeline from the manhole connection at “Todor Tower” on place 0 + 000,00 to tank in Cicevac on place 6 + 515, 00 is predicted the installation of polyethylene pipeline DN 400. The trench for the laying of the pipeline is rectangle cross section, width 1 m, with leaves distance of 30 cm from the out of edge of the pipe to the trench wall. For crossing the pipeline under the traffic arteries, the installation of the steel pipe DN 600 is predicted.

After excavation, on the bottom of the trench the layer of sand is predicted, thickness at least 10 cm. That also makes it possible the even pipeline lean on the ground.

Further filling means checked impressing in two layers. In the first layer the installation of specific material, sand, gravel or gritting material, with maximum grain of 20 mm and no more than 12% clayey – dusty fraction. This layer is covered in one step to the half of the pipe height. This follows checked impressing, according to technical conditions with remark, that is needed, after impressing, to place protective board near the pipes, for prevention the pipe damage.

After installation of the first layer, than the other is done with controlled impressing with selected material from the excavation, with maximal grain diameter to 20 mm. The height of this layer should be to 2/3 of the pipe height. The next layer is installed to the height of 20 cm above the pipe top, and it is made of the selected material from the excavation, without controlled compactness. The rest of the trench is fills with left material from the excavation.

For the lodging and protection of the equipment on the pipeline – air valves and muddy drainpipes, metal framework – concrete manholes are predicted. On the whole line installation of 21 manholes is predicted for different purpose.

2.3.1. Air valves and muddy drainpipe

Air valves work is totally automatic and it is connected on pipeline with outer atmosphere. Air valves consist of two chambers in which moving balls are placed. One chamber, on whose top the outlet is installed, serves for outlet the small quantity of air which is during the work separate from water. Swimming ball in that chamber is open automatic because of the work of the driving uphill so it opens and closes outlet for the air outlet. The other chamber on which top is the high diameter opening for the outlet of big quantity of gas, during the charging the pipeline with water and also it permit the entrance of big air quantity needed for the discharging of the pipeline. The ball in the other chamber opens and close the hole on the top because of pressure difference working. The other chamber is working only when the inner pressure is equal or smaller than outer, and on the other hand the first chamber is working all the time at full section state. When the pipeline is empty, the both balls are placed at chamber bottom so the both openings are free.

On the line, there are eight air valve manholes and nine outlet manholes.

Each of the valves is separated from the main pipeline with handy butterfly cover, with the suitable metal framework. Determined and encircled diameter values are unified on the section and they are DN 100 mm. Standard manhole of air valve of the pipeline are 2, 1 x 2, 0 x 2, 2 m and the thickness of the wall of 20 cm. On the whole pipeline air valves DN 50 are installed. For air valve installation the installation of T pieces DN 350/50 is predicted on which air valve DN is placed. For making air valve repair possible in front of the valve the installation of the flat bolt DN 50 is predicted.

Muddy drainpipe manholes are projected mostly with the chambers for the receiving outlet water which should be discharged by pumps in immediate closeness if there are conditions for that or water can be driven by the cisterns.

2.3.2. Metal framework on the pipelines

2.3.2.1. Butterfly valves on the handy drive

On the pipeline in the muddy drainpipe manhole the installation of the butterfly covers on the handy drive is predicted so the discharging is possible of some pipeline section. The covers are service and it is closed only in the case of the discharging some pipeline sections.

Important characteristics of the butterfly covers are: complete blocked, low investment and section costs, compact construction, with small built in space, small weight, small movement moment and reliable function in each position of the installation.

Butterfly valve with handy drive flange

Rotation board axis is eccentricity made which made possible the sinking of the beam in spite of blocked flat of the constant blocked ring. In the moment of opening, and on that way friction is reduced.

In the closed position elastic blocked ring on the valve board hardly leans on the metal ring of the casing and on that way it makes possible waterproof blocking in both direction of the flow.

Bolt flanges are of pressure NP 10. Connection  measures of the flanges are in standard JUS MB6 011 (DIN 2503).

Production material

- Valve body                               alloy steel cast (SG GGG)

- Seat body                                  austentic black steel

- Disk body                                 alloy steel cast (SG GGG)

- Blocked ring seat                      steel St 37

- Blocked ring                             elastomer (EPDM)

- Bearing case                              steel – maintaining not needed

- Connection bolt                        non-corroding steel A2, DIN 267

- Low–range gear lever casing    steel cast (GG 25)

- Low-range gear lever curve      steel cast (SG GGG – 50)

- Spindle                                     chromed steel

- Spindle nut                               hard bronze

- AKZ protection                        valve is AKZ protected with EKB coat of blue painting, RAL 5015

2.3.2.2. Butterfly valves on electric motor drive

For the flow measurer manhole the electromotor drive butterfly valve is predicted. The valve is also the regulation valve by which flow is regulated on the information from the flow measurer.

Built in measures of the butterfly valve are appropriate to JUS (DIN) standards: JUS M C 5. 005 (DIN 3202).

The flanges on the butterfly valves are appropriate to standards JUS M. BG. 011 (DIN 2503).

All valves in the lead covering are made of:

- valve body    alloy steel cast EN – JS 1030

- seat body      austentny black steel

- disc body      alloy steel cast EN – JS 1030/EKB

- blocked tire                       EPDM

- case                                  Acetal

- semering                           EPDM

- AKZ protection  valve is AK2 protected with EKB epoxy coat of blue color, RAL 5015

- Electro drive                            AUMA, SA 10, 1 – B1/90

Opening and closing of the valve is done by the button press.

Electro drive is prepared in Electro section of the project.

2.3.2.3. Valve (with short body)

On the pipeline the flat valve with short body installation is predicted on discharging pipeline. DN 100 and in front of air valve DN 50 installation flat valves with short body DN 50 is predicted. In covering of the tank the installation of flat valve DN 200.

The valve is used as covering during the pipeline discharging. The valve is mostly closed. It is open only when pipeline discharges.

The valve are made for maximal working pressure 10 bars. Built in valve measures are appropriate to JUS (DIN) standards JUS M C5. 005 (DIN 3202).

The valve flanges are of pressure NP 10. Connection measures of the flanges are in standard JUS. M. BG 011 (DIN 2503).

The valve is carried out with flanges and rigid valve wedge. Moving of the valve is handy done, with a wheel, by turning axial motionless spindle.

The box cabinet case, valve disk, block case and handy wheel are made of grey casting.

Blocked rings and spindle nuts are made of bronze.

2.3.2.4. Assembly and disassembly part

Assembly and disassembly parts are used as elements for connecting because it makes it possible easier and simple installation of metal framework pipe elements using possibility for adopting install length in limits +/- Δ 1. Flanges of assembly and disassembly parts are PN 10 pressure. Connection flange measures are in standard JUS. BG. 011 (DIN 2503).

Assembly and disassembly flange is of: flange, pulled in flange and tighten piece.

Blocking is achieved by tighten of blocking element, “0” ring tighten piece.

Flange, pulled in flange and tighten piece are made of quality steel cast.

2.3.2.5. Automatic intake

On the pipeline eight manholes are predicted in which automatic intake air valves DN 50.

Intake air valve serves for correct pipeline work and makes possible: air removing from pipes before releasing section to work, air removing from pipes which separates from water during the work, prevent appearance sub pressure during the discharging the pipeline or stopping water flow because of nonstationary regime.

The valve work is totally automatic and it connect pipeline with outer atmosphere. During system work there is no loss of water on the valve. The valve is consists of two chambers in which two moving balls are placed. One chamber, on which valve outlet is placed, serves for discharge of small air quantity which separates from water during the work. Swimming ball in that chamber separates automatic because of working of driving uphill so it opens and closes outlet for air discharging. The other chamber, on which cover is hole of big diameter serves for discharging big gas quantity during the pipeline charging with water, and also it lets the entry of big air quantity needed during the pipeline discharging.

The ball in the other chamber opens and closes valve hole because of working of pressure difference. The other chamber works only when inner pressure is equal or smaller thin outer, until the first chamber works all the time at full section state. When the pipeline is empty, the both ball are placed on the chamber bottom, so the both holes are free.

Box cabinet case, box cabinet case covers are made of grey cast. The balls are made of steel valve with rubber.

2.3.2.6. Flow measures

On the pipeline behind the manhole connection the electromagnet measure DN 350 PN 10 is predicted.

The flow signal is directed to butterfly valve on electromagnet drive which is placed in flow measures manhole so the regulation to Cicevac tank can be possible.

Measurement of the electromagnet flow measure is based on Faradey law electromagnetic induction. Electromagnet flow measure consists of two basic pieces: giver for making magnetic field in the pipe and electronic device for power, reinforced processing of the signal.

Technical characteristics

- measure range is 0 – 100 L/S  0 – 80 L/S

- point of sensitiveness 0,1 – 1,0 mm/s

- testing pressure 1,5* NP

- working temperature T min = - 40⁰C, T max = 150⁰C

- inner covering of the giver: manufacturer recommendation in conformity with chemical water structure

- minimal fluid conductance ≥ 5 μS/cm

- protection IP 67 (IEC 529 or DIN 40050)

- current outlet 4 – 20 mA

- exact of measurement (V ≥ 0,5 m/S, measurement error is +/- 0,5% of the flow)

- the sink: sensor must always be complete full fill with water.

3. THE TANK VARVARIN

3.1. Introduction

The installation of the tank, volume V = 2 x 2000 m³, is predicted with pour point on 196,00 mn. m. The tank “Varvarin” is consisted of two separate water chambers with total volume V = 2 x 2000 m³ = 4000 m³ and with one together closing. The height of water 4,00 m with pour point on point 196,00 hasl m.

3.2. Water chambers

In the base, water chambers have inner dimensions 22,50 x 22,50 m and with inner height of 4,50 m. Water chambers are projected from waterproof reinforced concrete. Lower board has height of 30 cm, walls have width of 30 cm, and upper board has height of 25 cm. Lower board concreting of one water chamber must be done in one move, without interruptions. The water chamber walls also must be done in the same way to the upper board. Iron casting pipes which enter in the tank chambers and casting – iron creepers installed before concreting in the plating vertical walls on marked places. Before upper board concreting install ventil head as marked in the project.

Water chambers have nine supports, placed on axis distance of 5,70 m haunch with dimension 1,8 x 1,8 m and the height of 0,6 m. Support dimensions are 30 x 30 cm and with height of 3,30 m without haunch. Between supporters chicaneries are projected, made of unreinforced concrete, width of 15,00 cm and height of 4,25 m. Inner surface of outer walls and lower board are coated with penetrates.

Outer surface of water chambers are completely protected with waterproofing which consist of one coat bitulit and with three layers of condor strip which by spreading cast all its surface.

Protection of vertical isolation from mechanic damage with brick wall width of 12 cm. On upper board, form layers for fall of average height 10 cm over which waterproofing is done. Layer of ground which fills on upper board is 60 cm. Fill ground slope do in slope of 1 : 1,5.

3.3. Foundation

Founding of foundation boards is predicted on the layer of thick gravel d = 20 cm and on the layer of thick concrete height d = 15 cm. Before placing tampon gravel layer and thick concrete control geodetic heights. If the ground is dig up, increase tampon gravel layer with equivalence stamping. If the height is not enough finish digging.

3.4. Valve chamber

In the base gate valve case inner dimension 6,40 x 3,70 m and it is division on two floor. Lower floor is high 4,55 m and upper is 2,80 m. Lower board is 20 cm high, walls are width 20 cm, and middle and upper board are 15 cm high. Walls have to be done in smooth plating. Lower floor is on the point 190,30 mn. m. and upper floor is on the point 195,00 mn. m. From upper floor to lower floor there is a stairways of width 80,00 cm. In the board on the point 195,00 mn. m. is placed the assembly hole, dimension 1,45 x 1,00 m. This hole closes with locksmith’s cover which has frame which is fixed in concrete board over anchor discharges. Entrance to the closing are 100 x 200 cm and it is projected to be locksmith left door, and it has fixed blinds 80 x 60 cm and which is equipped with needed shackles and lever lock. Holes between water chambers and closing are 1,00 x 1,00 m and they are closed with locksmith windows. Locksmith fence is fixed on stairways side with steel RB wall in – lay so the more space on the stairways is left. All metal parts make minimum and paint in to layers with epoxy color for metal in chosen color. From the board on the point 197,95 mn. m. drain is placed. Complete ring and closing discharge border with zinced sheet metal d = 0,65 mm. Around complete tank drainage is projected from PVC drainage pipes DN 160 which pour in drainage manhole 1, and from that place to the sink head.

3.5. Assembly works

Complete metal framework in tank closing is on flange connection for NP 10 bars. Valves are like butterfly, and they have low-range gear lever on it and also they are handy driven. Level water regulation in water chambers is done by level regulation and its float which is placed in water chamber. Irretrievable clapper is like butterfly with contra weights. Pipe connections are projected in that way that can carry out complete set of ductil phase pieces. Water is bringing by pipes which has diameter DN 400 where is separate on two pipeline DN 300, to both of water chambers. Water drain is by pipeline DN 400 which doesn’t have stops. Drainpipe has the diameter DN 150 and pouring pipe DN 300. Maximum quantity of water which can enter the tank is 90 l/s. After kuter for pipes of the circle cutting under fill of pipes 0,9 D for DN 300 and fall of J = 2,0% is 119 l/s which satisfied realization maximal pour water. Drain and pour water are pouring in private manhole 1, and from there by drainage pipes DN 350 to pour head. On upper floor level one rail lift is projected with capacity of 1,5 t with mobile handy drive carriage. Lift is intended for vertical transport in the closing. All metal part must be anticorrosion protected with one coating minimum and with two coating of epoxide metal color.

B) GENERAL TECHNICAL CONDITIONS

1. PRELIMINARY WORKS

1.1. General

Preliminary works for production pipeline and drainpipe installation are divided on preliminary works for pipeline and drainpipe in the object and preliminary works out of the object.

1.2. Preliminary works for pipeline and drainpipe in the object

Preliminary works for pipeline and drainpipe in the objects are divided on nine categories depending on number of pouring places in objects:

- object to 50 pouring places

- object from 50 to 100 pouring places

- object from 100 to 200 pouring places

- object from 200 to 300 pouring places

- object from 300 to 400 pouring places

- object from 400 to 500 pouring places

- object from 500 to 700 pouring places

- object from 700 to 1000 pouring places

- object over 1000 pouring places

Under preliminary works we consider the following:

- coming out of the work group on the object with tools

- tools and material storing in the warehouse

- examination of the technical documentation

- knowing of the object

- leading installing group into the work

Account for preliminary works for pipeline and drainpipe in the object is done by the object.

1.3. Preliminary works for pipeline and drainpipe out of the object

Preliminary works for pipeline and drainpipe out of the object are divided on four categories depending on the length of water:

- object to 500 m water length

- object from 500 m to 1000 m water length

- object from 1000 m to 2000 m water length

- object from 2000 m to 3000 m water length

Under preliminary work we consider the following:

- coming out of the work group with tool on the object

- tools and materials storing in the warehouse

- examination of the technical documentation

- knowing the object

- leading installation group into the work.

Account for the preliminary work for pipeline and drainpipe out of the object is done by the object.

2. EARTHWORKS

2.1. General

Before the beginning of the earthworks ground must be clean from coils, trees and roots. If the humus layer is used later, than coils, trees and roots on down on water and take care of them until use.

All earthworks are divided in seven categories:

I category:    loose soil, soft soil, clean sand, tied gravel, humus, loose plants and soil not tied. The most needed digging and throwing off with shovels, or spades if it is needed.

II category:   fertile soil, softer sandy soil, easy sandy clay – clay sand, compressed sand and small gravel, in soil without inner connection. Digging is done by spades.

III category: hard and tough soil, rough semi connected gravel, meadow soil and natural wet clay with small percentage of sand. Digging is done by spades and pickaxes.

IV category:  stones of the transitional formation in decay, marl states, soft and decayed lime stones, soft sandstone, conglomerate, quartz slates. Digging is done by crowbars, wedges, pickaxes and periodical by explosive.

V category:    soft stone (middle firmness), firm sandy soil, conglomerate, limestone, firm volcanic tuffs and all burst with massive stones. The breaking is done with crowbars, wedges, pickaxes and periodical by explosive (gunpowder).

VI category:  firm but brittle stone, big massive limestone, marble, dolomites, sandy soil and conglomerate of thick layer and good cemented, in the most magmatic stones, garnet and diorite magma, in gneiss in inlayer’s quartz. The digging is done only with explosive (dynamite).

VII category: very firm and root stone, fresh basic and ultra basic magma stone as – granite, basalt, quartz. The breaking is done only with explosive (dynamite).

Soil characteristics table

| Soil category | Soil category name | Tools used for digging | Coefficient of loading temporary increasing | Permanent increasing of volume |
| --- | --- | --- | --- | --- |
| I | loose soil | shovels | 1,15 | 0 – 2 % |
| II | plain soil | spade | 1,20 | 2 – 4 % |
| III | firm soil | hard spade and pickaxe | 1,25 | 3 – 5 % |
| IV | fragile stone | pickaxe | 1,30 | 4 – 7 % and more |
| V | soft stone | gunpowder | 1,40 | 8 – 10 % and more |
| VI | firm stone | dynamite | 1,50 | 10 – 15 % and more |
| VII | very firm stone | dynamite | 1,50 | 10 – 15 % and more |

Soil category income in account by the previous price, but it real categories will be consolidate during the works.

Before start digging profiles must be taken because of account.

When is about excavation, it is determined the way of digging for excavation to have symmetrical figure.

Use the loan which is near.

Account for the excavation is done by the taken profiles, after leveling is assured that the excavation is done on the necessary depth.

2.2. Handy excavation in the wide excavation

2.2.1. Work description

Handy excavation in the wide excavation after standards means work with shovels, spades, pickaxes or explosive, depend of soil category. The worker must dig soil with one of these tools for work and throw off or load it in transport wheels: seeker, carriage and dolly.

The excavation must be done under given measures taking carry that the sides of the excavations must be sharp, and the excavation bottoms flat to the level ± 5 cm.

Under wide excavation we consider all excavation which base is under 20,00 m² and it is not related on object foundations, septic tank, channel trench.

2.2.2. Account manner

Account manner is by 1 m³ of excavation on the base of profile taken before and after the excavation. Normative are given for work in natural wet soil and also in moist soil as in soil with roots. In the case of breaking in surface water in the excavation, contractor must put out water with available tools on his expense. Under concept of excavation in wet it means excavation in the case of breaking underground water. Soil category and excavation are defined by supervisor by inspection on the ground. Geodetic works by which the ground is recorded before and after the excavation account through unit price of the excavation.

2.3. Hand excavation for channel of all wideness and excavation which don’t belong to category of excavation in wideness excavation

2.3.1. Work description

Digging is done with one needed tools with symmetrical sides cutting and needed points of the bottom with exact of ± 5 cm. Excavated ground throw from excavation edge on the distance of 1 m. On the depth, more than 2 m, digging must be done gradually taking excavation material by shovels or handy from ferry to ferry.

2.3.2. Account manner

Account manner is by 1 t of excavation calculating after lamellas from 0 – 2; 2 – 4; 4 – 6 and 6 – 8 m of the depth.

Normative are given for work in natural wet soil, also in moist soil and in one with roots. In the case of the breaking surface water in the excavation, contractor must put out water with available tools by his expense. Under concept of excavation in moist soil it means the excavation in the case of the breaking underground water. Soil category and excavation are defined by supervisor by inspection on the ground. By normative is also considered the work between brace also moving of the working ferry (platform) made of boards, which serves for moving dig material.

2.4. Covering and stamping down

2.4.1. Work description

Under his position spreading of material is considered with shovels and stamping down to needed compactness. The worker must spread material and cover material to the distance of 3 m. Material transport is not considered.

2.4.2. Payment manner

Payment is account by 1 m³ of spread material. Normative is divided in five categories:

- handy stamping down of soil in layers of 10 cm by ram of 10 kg to needed compactness

- handy stamping down of soil in layers of 20 cm by ram of 10 kg to needed compactness

- handy of soil in layers of 30 cm by ram of 10 kg to needed compactness

- handy stamping down and covering without stamping down

- mechanical stamping down by vibrating – plate.

2.5. Planning

2.5.1. Work description

Planning considers ground planning with exact of ± 3 cm with average excavation of 0,05 t/m² and transport of needless material to the distance of 50 m.

2.5.2. Payment manner

Payment is accounted by 1 m² of planned ground. Geodetic works needed for planning are not accounted.

2.6. Mechanical excavation with the dredge

2.6.1. Work description

Under mechanical excavation with the dredge means the excavation with direct loading in the transport wheel. It is not allowed digging up, excavation with the dredge under needed point.

2.6.2. Account manner

Mechanical excavation account is done by 1 T excavated fertile soil. Unit price include the price of renting of the dredge.

3. ASSEMBLY WORKS

3.1. Polyethylene (P.E.) pipeline pipes

3.1.1. Work description

In assembly position of PE pipeline pipes it is considered taking pipes from the waste 50 m distant from the place of putting down in the trench and pipes assembly. It is considered for all pipes handy taking and putting down.

PE pipes connect in pipelines with connected and unconnected joints (JUS G. C. G. 685).

In unconnected joints we include:

1. Joints with clips

1.1. PP clips with nuts for small thickness PE pipes

1.2. Cogged clips with pipe nuts for big and small thickness PE pipes

1.3. Collars from casting iron for big and small thickness PE pipes

2. Joints with flanges

2.1. Joint with free flange and casted tube for big thickness PE pipes

2.2. Joint with free flange and cogged flange for big and small thickness PE pipes.

In connected joints we include:

1. Joint with head cast for big thickness PE pipes

2. Joint with head of small thickness PE casted on pipes by special heating element

3. Joint with head of big thickness PE casted by resistant spiral heater.

Pipe connection with standard phase pieces and with special phase pieces from casted iron can be done as flange joints or with clips with pipe nuts. Smaller profiles of PE pipes are very interesting because they successfully change iron zinced pipes for disposable receptacle production.

Putting down

- During assembly we must consider the difference which may occur because of temperature difference. Length changes are 16 times bigger at big thickness PE pipes than at iron pipes.

- Trench width is determined to by diameter of the pipes W = DN + 2 x 20 cm, and the minimal trench width is 0,60 m if the pipe is putting out of object and if the pipe is putting in, than trench width is 0,40 m.

- Depth of putting the pipeline depends of climate conditions. In our country the depth shouldn’t be less than 80 cm from pipe head to ground surface.

- Pipe must lay in the trench by all its length and on material as sand clay and similar materials, without rocks.

- During covering of the trench, the first layer under the pipes of 30 cm must be from the same material as bed. Before covering, material must be stamped down with 10 kg ram to needed thickness of 0,5 m high from the pipes, and after with vibrating board.

- Further covering do with material from the excavation in 30 cm layers.

3.1.2. Transport

PE pipes are delivered, depends of profile, in circle of 200 and 100 m and in flat pipes of 6 – 12 T. They may transport by all wheels.

3.1.3. Account manner

In position of PE pipeline pipes it is considered taking pipes from the waste 50 m distance to the place of putting to the trench, unwinding from circles, putting pipes in the trench and pipe assembly. Handy taking and putting is considered. Trench must be dry.

Payment is accounted by 1 m of pipes. In the case of hard condition, (work in wet, work between brace), work is accounted additional. In the price is accounted all working team and all material also.

3.2. PVC drainpipe assembly for outer drainage

3.2.1. Work description

In the position of PVC drainpipe assembly for outer drainage it is considered taking pipes from the 50 m distant waste to the place of putting in the trench, putting pipes in the trench and pipe assembly. For all it is considered handy taking and putting. It is also considered that the pipes are 6 m and putting in dry trench.

The way of pipe assembly is the following:

- Trench width is determined after pipe diameter  W = DN + 2 x 20 cm, and the minimal trench width is 0,60 m

- Pipe putting depth depends on climate conditions and outer pipe load. In our country, the depth shouldn’t be less than 80 cm from pipe head to the ground surface. The depth of putting pipes is accounted depending of static ground load and dynamic, traffic load.

- Pipe must lay in the trench by all its length and on material as sand, clay and similar materials, without rock.

- During covering of the trench, the first layer under pipes of 30 cm must be from the same material as bed. Before further covering it must be stamped down with handy 10 kg ram to the needed thickness.

- Further covering of the trench must be done with materials from the excavation in 30 cm layers with stamping down with 10 kg ram to 0,5 cm from the pipes and after with vibrating board.

- During connection of pipes sleeve must be cleaned, rubber block must be formed in heart shape and put it in sleeve, askance part of the other pipe coat with slipping funds ( Caley’s soap ) and with easy movement askance and put into the sleeve to the end and than put it out to the marked border, if there is, and if there is not, than to cca 5 mm.

- PVC pipe assembly can be done out of the trench and put them down after ( in colder, winter conditions that is not recommended because of brittleness of the pipes ). At PVC pipelines some deviations are allowed from the line.

- During the breaking pipes through the wall of the concrete manhole, pipe must protect with rubber blocked ring by which we protect pipe from damage from concrete, and also we block joints between concrete wall and PVC pipes, because concrete doesn’t connect with PVC.

3.2.2. Transport

PVC pipes transport may be done with all kind of wheels. During transport, pipes should lay by all their length. If pipes stick out of the wheel, they must be protected, because they mustn’t “seesaw”.

Together with pipes other sharp things shouldn’t be transported. During loading and unloading the pipes shouldn’t be thrown.

PVC pipes and phase pieces mustn’t be pulled down the ground. At low temperature PVC pipes are sensitive on strikes, and in cold condition, take care about that.

During storing, maximal height of storing is 2 m. Sleeve and slope end of the other pipe should be one to another. Pipes shouldn’t be long at the sun. Long exposing on the sun, PVC pipes loose color but quantity not.

3.2.3. Payment manner

On the position of PVC pipes assembly it is considered taking pipes from the waste 50 T distant from the place of putting pipes into the trench, leveling and assembly of the pipes. Handy taking and putting down is considered. Supposed length of the pipes is 6 m, also putting down in dry ground.

Payment is accounted by 1 m of the pipe. In the case of hard conditions (work in wet, work between brace is accounted separately. In the price working group and all needed material is accounted.

3.3. Iron - cast pipeline phase pieces assembly

3.3.1. Work description

In the position of iron – cast pipeline phase pieces it is considered taking phase pieces to the place of storing to the place of assembly, maximal distance of 50 m, putting phase pieces down to the trench, placing gasket centering phase piece and stretching of the bolt.

3.3.2. Transport

Iron - cast phase pieces may transport with all kind of wheels. During loading and unloading must take care of the phase, pieces not to fall because they can break. For phase pieces of 50 kg handy taking and putting into the trench is considered, and for heavier phase pieces use lifts.

3.3.3. Account manner

Paragraph iron - cast pipeline phase pieces assembly is account by 1 kg of the phase piece. It is considered the work in dry ground. If it is hard condition for work (work in wet, between brace) on one paragraph price for work in hard condition is added.

3.4. Iron - cast pipeline metal framework assembly

3.4.1. Work description

In the position iron – cast pipeline metal framework assembly it is considered taking metal framework from the storage to the place of installation, maximal 50 m distance, putting metal framework into the trench, placing gasket, centering metal framework and stretching bolts.

3.4.2. Transport

Iron – cast pipeline metal framework may transport with all kind of wheels. During loading and unloading must take care metal framework not to fall because they can broke. For metal framework to 50 kg handy taking and putting into the trench is considered and for heavier use lift.

3.4.3. Account manner

Every paragraph of the iron – cast pipeline metal framework is accounted by 1 framework piece. The work in dry ground is considered. If the work is done in the hard condition (work in wet, between brace on the paragraph price for work in hard conditions is added.

4. BUILDING MATERIAL TRANSPORT

4.1. General

Material transport with normative:

- handy transport without equipment

- by seeker or trough

- by carriage

- by japaner

- by transport line

- by transport lift

- by skip

- by crane

- by highline cable

- and loading and unloading of material to the wheels.

Material transport is done:

- along horizontal or gentle leaned surface

- along lean (to 30 %) on the height or depth

- vertical on the height or the depth

4.2. Loading

- By putting down- piece by piece load into transport wheel, trying to use most of the transport wheel and not to damage.

- By throwing onto- load with shovels, pitchforks or by hand from ground to the transport wheel.

- From storage space- materials fall by itself to the transport wheel (from the storage space).

Transport wheel placed 1- 2 m distant from the loading place, and in the time norm lifting and putting down to 1,5 m is accounted.

4.3. Unloading

- By taking off (stacking) – take off piece by piece from the transport wheel to the ground so materials is not damaged, taking the smallest space.

- By throwing – throw material by shovels and hands material from the transport wheel to the ground.

- By handing over (turn over) – handy over material from the transport wheel by turning over on the unloading place.

Transport wheel placed 1 – 2 m distant from the loading place and in the time norm lifting and putting down to 2 m is accounted.

4.4. Account manner

Payment is account by 1 m³, 1 t or by piece depending on kind of material which is transported.

5. FINISHING WORKS

5.1. Pressure testing new built pipeline installation

5.1.1. Work description

- Pressure testing is test limited with time, with pressure which is higher than indicated pressure. Testing divided on: short testing (I, II, III), earlier testing, main testing and gathering testing. If it is not possible to test the pipeline at once, than, test it in sections. In that case, joints between sections test on waterproof by gathering testing.

- Testing is done on sections 500 m long. If there is big high differences, such part of section must choose so the working pressure may be achieved.

- Before pipeline testing on pressure, the pipeline must anchor on every place of line breaks and pipeline working. Testing pressure and capacity of the ground on pressure and sliding must be considered. Pipelines cover and in the case of inner installation tighten to wall, but all joints must stay visible. The pipeline charges with clean water and discharge all air. Pipeline charging is done from the lowest point. Lifting pressure pump is placed on the safety place. From the testing time any work or staying in the trench are not allowed because the pipes can crack.

- For testing manometers are used. They must have splitting so that change of 0,1 bar can be read. Two measures instruments are recommended, one is only control. Manometer is placed on the lowest point of the testing pipeline section. With pressure, quantity of water is measured, which is added because of temperature and elastic expanding of the pipeline.

- If same place which leaks (drops, steams) appears on testing sections, the testing must stop and the section must empty. On leak places water must discharge total. Testing can continue after repairs.

- Record must be taken about pressure testing and one copy goes to the investor and the other to the contractor.

5.1.1.1. Short testing I

That test is taken on the short pipeline (connection for house to 15 m). Do testing of pipeline and joints under working pressure.

5.1.1.2. Short testing II

That testing is taken on the short pipeline to 30 m (longer connection for house). The pipeline put on pressure 1,5 x working pressure. After 30 TT testing begins, without any increasing of pressure of 30 TT drops. After starting testing pipeline pressure mustn’t drop every 5 TT for more than 0,2 bars. Testing lasts for 60 TT.

5.1.1.3. Short testing III

That testing is taken on the pipelines without among elements (connections, phases, metal framework), over 30 m. The pipeline puts under pressure of 1,5 x working pressure. After 2 hours, the pressure which is dropped needed to increase to 1,3 x working pressure. After more 2 hours, testing begins, without increasing of pressure. After starting testing we can count of dropping of the pressure for 0,2 bars per hour. Testing lasts 30 TT for every started 100 m of the pipeline, at least 2 hours.

5.1.1.4. Earlier testing

Testing is done on pipeline section with among elements (connections, phases, metal framework) to 500 m. From pipeline air must be discharged. Air which stay in pipeline discharged with water from previous testing. The pipeline expands depending on material of which it is made, so the volume increase should be taken from table of pipe material manufacturer. Testing pressure is 1,3 x working pressure. Earlier testing lasts at least 12 hours. In regular time interval (every 2 hours) the pipeline fills with water to the testing pressure. At the end of earlier testing, every 2 hours after last increasing of pressure, pressure drop is 0,1 to 1,2 bars per hour and if the pipeline is waterproof on all places depending of material and temperature changing.

5.1.1.5. Main testing

If, during the earlier testing on pipes, joints and metal framework do not appear leaking of water, and if the pipeline volume in the earlier testing increase as it is said, we can do the main testing, without dropping the pressure. Testing pressure is the same as at the end of the earlier testing. It is recommended that testing last 30 TT for every 100 m and at least 2 hour. And during the main testing, we must take care of expanding of the pipeline, which is not finished completely. We suggest that the main testing starts 2 hours after the last increasing of the pressure in the earlier testing. Testing is finished if there is not occur pressure dropping more than 0,1 to 0,2 bars per hour and if there are not places which leak.

5.1.1.6. Gathering testing

Joints places between testing sections are testing. It must be short testing and main testing. Joint places mustn’t be covered. Testing pressure is 1,3 x working pressure. Testing lasts for 2 hours.

5.1.2. Account manner

Payment is accounted by 1 m of done pipeline profile. Price include preparation of pipe net for the test, placing plugs at inner installation, placing testing pump on working place, charging of pipeline with water, marking leaking places, repair leaking places, taking register about net testing, discharging of the pipelines after testing.

5.2. Drainpipe installation testing

5.2.1. Outside drainpipe

Drainpipe before covering need to be tested so the quality of work in waterproof can be proved. In good work, mustn’t be infiltration or exfiltration.

Table of allowed quantity of leaking water

| m³/24h/km | 7 | 12 | 15 | 18 | 20 | 21 | 22 | 23 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pipe diameter | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 |

5.2.1.1. Pipeline in ground with underground water

If the level of underground water on 2 – 4 m above head of the pipe	 quantity of water which enters the pipe mustn’t be more than values shown in the table of allowed quantity of leaking water. When the level of underground water is more than 4 m allowed quantity of infiltrate water increase for 10 % on every meter above this level. Infiltrate water measurement is done by measuring quantity of water which flow out on downstream end of the pipe through testing faucet in time of 30 minutes and do the account on 24 hours.

5.2.1.2. Pipeline in the dry ground

Drainpipe between two revision manholes fills with water to 4 m under pipes head. Allowed water loss mustn’t be higher than values given in table of allowed quantity of leaking water. Exfiltration measures with quantity of water which fills in 30 minutes in order to maintain testing pressure and it is accounted on every 24 hours.

5.2.2. Inside drainpipe

All drainpipe holes close, except the lowest and the highest hole. On the lowest point of installation, pipe for charging installation with water assemble. After installation is full until the highest point the hole is closed and installation fill with water to testing pressure of 4 m water column above the highest hole. After 30 TT the quantity of water is measured which is needed to achieve testing pressure. Received quantity of water is accounted on 24 h and if it is less than 0,005 l/m installation is good.

5.2.3. Account manner

Drainpipe installation testing is accounted by pipeline profiles by m.

5.3. Washing out and pipeline installation disinfection, tanks and pumping pools

Line pollution may come from dirty of pipes and parts which are built in and also from break through dirty (sand, soil, mud, dirty water from the trench…) during working of pipeline putting in.

From those reasons, for the process of washing out and disinfection is easier, we must take care to use clean pipes, fittings and metal framework.

In the event that is water in the trench, it needs to be pump out during the laying of the pipeline. 
At the termination of works on passing the exam required to be a wooden stopper closed end tubes. This also prevents the entry and various animals (mouse, rat, ferret, hedgehog, cat, etc.) in the pipeline. 
Tank chambers are also often pollute at the building. So in addition to sand, mortar, waste of the board may in running water to the broken left open the embedded pipe pieces, if not closed caps, dirty water with earth and mud. 
For this reason it is required by building completed tank Chamber to make from the same side of all the materials and conscientiously clean broom. 
Disinfection of interior surfaces of new or repaired pipe is considerably heavier than the disinfection of water polluted because Chlorine must have broken through the organic matter, which is covered by the inner surface of the walls of pipes. 
To obtain good results it is necessary to previously cleaned and rinsed well pipeline and chambers of the pumping pools and reservoirs.

5.3.1. Washing

Laundering of the pipeline be accessed after the hearing of the trial pressure, a washing tank chamber  only by the technical receipt. 
Washing is only allowed to use the correct water market. Washing is effective only if it provided a minimum water velocity of 1.5 m / s. 
How to make washing depends on the number of discharges. 
No one may cause any damage with the released water during laundering. What about this solution is not given in the project supervisory authority is obliged to have that solution directly on the ground. Washing should be continued all the time until it gets completely clean water to drop. 
During this washing, it is necessary to periodically monitor the quality of water to drop, so as soon as you stop that emerges muddy water, or when it appears completely clear water, the washing is complete. If this time of washing lasted less than 20 mp, washing should be extended until this time to the amount of water used for washing reached approximately threefold volume of shares that are wet, which is commonly used in practice. 
The amount of water for washing (min. norm) should be counted:

- Up to DN 150 3 to 5 - the capacity of the section that is being washed

- Through DN 150 2 to 3 - the capacity of the section that is being washed

Washing tank is carried out together with the recent section of the pipeline that goes in the tank. Water suppresses the last section in the tank, with a speed of 1.5 m / duration are 30 TT after which time the wash has finished. 
If the water in the chamber is very muddy, it shall be left overnight to dispose. Then on the pipeline opened the shutter to drop and let the water opposite direction from the last rinse tank section. This release takes the appearance of clear water to drop. If the outlet is still turbid water, stopped releasing water from the chamber when the water level in the chamber down to about 0.30 m from the bottom. Then the shutter closes at the exit from the tank, opens the shutter on the mud drop, down workers with clean boots in the chamber, which is constantly stir, and using the broom, he is cast from the bottom of the water chamber with mud. Then the shutter closes the mud discharges and repeating the previously described procedure.

5.3.2. Disinfection

To and after the making of washing all possibly arrears of organic matter and organisms destroyed and that the supply tank and the chambers were by the quality of such water at the march and accumulate in the chambers retain their validity in terms of bacteriological, will be necessary to carry out and disinfection of these objects. 
To make this disinfection able to perform fully the need to water with a certain dose of Chlorine stay in the pipeline tank and chambers around 24 hours. 
Disinfection means shall prescribe sanitary services of the Water Supply and in conformity with the sanitary inspection of the city. Control of washing and disinfection performed solely under the direction of responsible, qualified and authorized representative of sanitary service companies. 
Chlorine dose for disinfection should be moving within the limits of 30-200 mg / l. It is considered that the 30-50 mg / l. 
In this case dose prescribes authorized representative of sanitary inspection, which is in general responsible for the disinfection and possible consequences. 
Lower concentration is recommended when Chlorine remains in contact with 12-24 hours. 
During normal operation Chlorine lasts 3-12 hours. Chlorine larger doses are used when it is known that the pipeline contains organic matter, which is impossible to remove the washing, or when it is necessary to shorten the time of disinfection. 
Minimum time of disinfection should be is 30-60 min. Adding Chlorine can be carried out through the initial hydrant or particularly left port. Release of water is carried out on the downstream hydrant until chlorine is not clearly felt. 
Parts of the network that is not disinfectant must be safely excluded from part of a network that is disinfectant. 
Responsible Head of sanitary services should provide and the protection of workers who work on disinfection, since Chlorine is hazardous to health if not handled carefully with him. 
Responsible manager should also ensure (through public notice, etc.) to avoid that someone uses the water that is used for disinfection. 
The completed chlorination must take the minutes, which certify person under whom the control of disinfection is carried out. 
With chlorine water pipeline will fill all chambers reservoir to a height of approximately 0.40 m from the bottom. Depending on the dose Chlorine's water will remain in the buildings 12 to 24 hours. By inclusion of pump sets and hypo chlorinator and their work in time of about 1 hour and it is stopped. In each tank chamber descends two workers with masks, rubber boots and rubber gloves to each connected, with what should be two workers to stand outside in manholes and keep the ropes regions that are related to workers and monitor the movement of workers in the tank . If you notice that the workers in the chambers have problems now will help to get out. 
The chamber workers need a new broom with chlorine water as urgent to rinse the walls, ceiling and the stairs and promptly leave the Chamber. 
At the entrance of workers from the chamber, chambers are closed covers and leaves chlorine water to stand in them 12-24 hours. Likewise, so should chlorine water to remain in the pipeline. 
Upon expiration of this time, check the concentration of Chlorine. If it is that when it determines that the water contains about 10 mg liter Chlorine in the water, this is indication that the disinfection was performed successfully. And in that case, all over  chlorined water from the pipeline and tank chambers off. When you release the water chlorine should be noted that this is not fed through CROP because they would in that case destroyed. 
In the case of checking that the concentration of Chlorine adds to Chlorine in water has about 5 mg / l or less, it is necessary to repeat the disinfection.

5.3.3. Flushing

Flushing is done the same procedure as well as washing of the pipeline, tank and intake chamber. Flushing is done when  drinking water with Chlorine concentration of 0.5 mg / l. Flushing lasts until the drop does not establish Chlorine concentration in water of 1 mg / l or less. Upon completion of flushing of the pipeline tank and chambers are ready for inclusion in a regular drive.

5.4. Geodetic Survey route new built plumbing and drainpipe network

5.4.1. Description of work

Work consists of surveying the Recruitment Team, which is published on the ground, measure the coordinates of all points of the fractured route, crossing the other objects (other underground installations, pavements, roads, etc.) and depth of the pipeline, the same data processed in the office and submitted a written report and sketches necessary for amending the cadastre of underground installations.

5.4.2. Method of calculation

Geodetic Survey route of the new build plumbing and drainpipe network is calculated by m 'the recorded route.

6. CONCRETE AND REINFORCED-CONCRETE WORK

6.1. General

Concrete and reinforced-concrete work must be run by the applicable technical regulations and standards in conformity with the mandatory standards of the Yugoslav (JUS). 
Materials must match the quality of technical regulations and standards JUS. Particularly emphasize the following standards:

• cement JUS B.C1.010/B.C1.011/B.C1.012 
• bar JUS C.B0.500/C.B3.021/C.K6.020/C.K6.021 
• water JUS U.M1.014

Anticipated items of the measurement for concrete work include in addition to creating and supporting papers such as:

• Works on the protection by the legal provisions on protection at work, 
• cleaning and wetting board immediately before the start of concreting, 
• repair its hull during concreting, 
• preparation and embedding concrete, 
• clean room and machine after completion of works, 
• protection and the concrete.

Prior to commencement of work must be prepared foundation holes, form work and reinforcement. Concrete should be installed in layers of 15 cm thick and jam until it breaks out on the water surface of concrete. Interruption of concreting steps to make a better link. Concrete is mixed exclusively mechanical, and code embedding stamp down mechanical means (vibrators and per vibrator). 
For all elements where necessary form work same time need to set a good support and unsupported that would not have occurred during the concreting of the enlargement, stricture, or any deformation of concrete elements. 
Before concreting form work should be well wet with water. It is also necessary before concreting cleaned the whole area inside the hull of the dirt, palette, etc., and clean broom and wash water. 
In the winter period should be concrete, well-protected from frost layer of cardboard, board, sand or otherwise. All care must be concrete in calculated Unit costs and will not be charged separately. The same applies to sun protection. 
All possible shaggy, flushed and frozen parts should be removed from the healthy area and the part to perform again, but without a charge. Contractor is required during the construction to take the test cubes from each specific structure, according to existing regulations, but also by seeking the supervisory bodies, and they deliver at a specific time for examination. 
While lots of the building, must be exposed to the same catch as well as the construction which is made of the same concrete. 
All material should be before you start work on concreting given for examination. 
All heights must provide and control the instrument. 
Stamp concrete, which must be built solely by static budget. Concrete must be made in the concrete mixer with the prescribed dosage of all ingredients of concrete, or concrete mixing plants. 
Brand concrete should control by sampling, i.e. creating a test cube in the prescribed iron casts. 
When making test cubes to comply with the applicable technical regulations. All costs of making test cubes falling at the expense of the Contractor. 
If the depth of embedding concrete greater than 1 m, the mandatory use funnel concrete to prevent segregation. Particularly take into account when the concreting of the armature remains in the position anticipated project. Reinforcement should be on all sides coated concrete. No one may begin with the concreting of the supervisory authority has reviewed reinforcement and writing in the daily construction verifies reception armature. 
Plating is done according to the technical regulations for the carpenter work. Calculation of the reinforced-concrete structure is to be made by applicable regulations and standards in construction (if it is not, and are for the preliminary estimate otherwise specified). 
Unit price includes:

• all the required material, 
• all the necessary work on the preparation and concreting, 
• Protection of concrete from the cold, sun, etc., 
• protective measures, 
• fostering concrete.

In the event that the supervisory authority or building inspections prompted test termination, the cost of these tests are paid separately.

6.2. Cement

Cement must not be used immediately after production, but must be off at least 15 days. Also cement must not be older than 3 months, and the structure has to be dusty, with no blob.  on the site should be protected from moisture, and wind and warming, keeping it up to use on the premises with her raised floor or in silos. 
The use of portland cement JUS B.V 1011. 
Prices of cement, transportation and storage as well as papers relating to the handling of the cement should be covered by unit prices for concrete.

6.3. Stone aggregate

Stone aggregate has a greater strength of cement. Must not contain rocks that are under the influence of the breakup of the water. Mud ingredients affect the strength of concrete, as well as organic and other harmful admixture, according to the technical regulations for concrete and reinforced concrete. For this reason the contractor is required to regularly performs control testing of aggregates to the construction site as follows: 
• content mud ingredients in the aggregate, 
• Purity stone aggregate in terms of organic matter, 
• content is very fine particles in the aggregate (smaller than 0.09 mm), 
• content dusty particles in aggregates (smaller than 0.02 mm), 
• granumetric composition of each fraction, 
• the content of amorphous silicon in the aggregate, 
• the content of mica in the aggregate, 
• the moisture in the aggregate. 
Samples for control tests will be taken from bunkers near the mixer, or with the place that determines 
supervisory authority. 
What is life long time is stored in the open air, must be pre-use check that it is not contaminated or harmful dirty matter. 
Price of aggregate, its transportation, storage, testing and providing work related to the handling of the aggregate should be covered Unit price of concrete.

6.4. Water

As a rule of using water from the water supply network. For all other waters (except wastewater and marshes that are useless) test should determine the content and concentration of harmful substances. Water quality has to match the provisions of the Regulations for concrete and reinforced concrete.

6.5. Admixtures

Contractor can use a plug-determination, which increases building, improves firmness and pressure on the tension, as well as waterproof. 
Preparation of additives allowed only if they are tested and if the certificates of qualified labor organizations confirmed that they have declarated properties and that their use does not undermine the quality of concrete and reinforcement in all according to the requirements of the Regulations for concrete and reinforced concrete. 
For the preparation of individual concrete additives must obtain a special permit investors (if not provided for the project), and their cost as well as work with them need to calculate Unit cost of concrete.

7. CARPENTER WORKS

7.1. Terms

All the necessary materials to create a board that should be adopted carpenters in appropriate quantities and dimensions of the place is done by sawing materials (boards, flowerbeds, planks, nail, wire), and a maximum distance of 30 m from the place of sawing. 
With all kinds of work are indicated by thickness of the board and cross section  flowerbeds or planks needed for work. 
Standards is included in the work on board a motor of the making tester as well as manually. The Unit cost of inputs: 
• development board, 
• assembly, 
• dismantling, 
• cleaning, 
• extraction of the nail, 
• transfer form works from floor to floor, 
• pull the form works upon the completion of the work, 
• agreement on a specific place away up to 30 m from the hotel.

7.2. Construction

Form works must be made accurately by measures, as indicated in the drawings for individual parts of which will be concrete and accurate manner indicated support (supporters of iron or wood). Compliant form works must be able to submit an appropriate burden to be stable, well-starched and support, that would not have been a deflection or wrapped no matter the direction. 
All support is calculated on the amount of up to 3 m. In the construction in more Floors supporters to set up and fix, so that the burden of upper strut communicate directly to supporters who lie beneath them. 
All surfaces must be flat and horizontal or inclined, depending on how that description requires. 
Extensions of certain form works are not allowed to come out from the flat, so that by removal, visual surface structure must be flat and with sharp edges. 
Form works must be made so that you can easily remove, and that the structures are not corrupted.

7.3. Method of calculation

Methods of calculating each type of work is accurately indicated. When measuring the effect of taking the inner surface, i.e. visibility finished surface structures that are developed. Provide standards for each type of work are complex, i.e. include the works of creation to disassembling, with the necessary assignment and possibly the necessary additional (mobile) scaffolding. 
If necessary support the form works height over 6 m should use the load-bearing scaffold, as direct support of ordinary supporters is no longer economical.

7.4. Material

Is consumption of material in each kind of work - required materials (quantity of material) which is listed (as well as the quantity of material depending on the number of use). All material for formwork given as IV class material (material for formwork), and it is to this class and is calculated using. Using the data collection, as follows:

• 24 mm boards for formwork - 7 times 
• boards for formwork 48 mm - 12 times 
• prove - 40 times 
• flowerbeds for formwork - 10 times 
• flowerbeds to prove formwork - 40 times 
• flowerbeds for support - 20 times 
• wells poles - 20 times 
• boards for bracing - 10 times. 

8. METAL FRAMEWORKS

8.1. General

Metal frameworks works include:

• correct manual borders, 
• cutting with mobile or stable scissors, 
• cleaning of dirt, grease and rust that peel, 
• manually bending the metal frameworks table, 
• sorting the Day details, setting and bonding according to the draft, 
• transmission reinforcement vertically and horizontally with a maximum of 20 m.

In the preparation of reinforcement in all are required to keep the project, by way of association as well as the types and quality of steel. If the market has a problem with projected procurement of reinforcement, changes can be made only with the approval of the supervisory bodies and the consent of the designer. 
When necessary to mount the fittings distance of its hull. When concreting careful to avoid bending reinforcement and concrete to completely cover the reinforcement. 
Include only the reinforcement with the prescribed certificates. If necessary carry out quality checking.

8.2. Method of calculation

Calculation is done by 1 kg built fittings

9. BRICKLAYING WORK

9.1. General

With all the building full and walls covered both of the standards are all the delay (work in small and rather restricted areas, artificial light, etc.). All preparing mortar data are mechanically by a vertical transport of material given in the two alternatives, as follows: skip and cranes, while in the horizontal transport means indicated that the material transported. 
All extra work around the building, as:

• Up and transfers from department to department and from floor to floor light movable scaffolding (legs, planks) 
• Transfer of the building beds, 
• occasionally mixture mortar, 
• adoption of water for wetting bricks, 
• scaffolding and cleaning job after job completion, 
includes Unit price items of the bricklaying works.

9.2. Bricklaying used

Material need for bricklaying (brick, mortar, water) must be adopted builder in the immediate vicinity and in sufficient quantities. Paragraph building used provided that the builder Walling wall with regular connections with one of the envisaged mortar, whose joints have to be horizontal, and the mortar thickness 1 cm. 
The walls must be vertical, and the extra mortar, while still fresh, it must be trimmed trowel. 
Leaned walls (setting the base order by marking) is covered by the Unit-price item. 
All work is scheduled from the new brick normal format.

9.2.1. Calculation 
Calculation is done for masonry wall thickness d = 25 cm or more, per 1 m3 previously mentioned brick-clad wall, a wall thickness of less than 25 cm calculation is done by m2 previously mentioned brick-clad wall.

9.3. Preparation of mortar

Material required for preparation of mortar must be adopted worker in the immediate vicinity of machines. The adoption of the required materials included in the transport of the stockpile to the place of preparing, at the distance of 15 m. 
Extraction of lime from the limekiln, if it does not work with moisturized move encompasses the Unit price preparing mortar. All mortar must be prepared to stipulate to provide a scope, well mixed and without any ingredient that it does not belong.

9.3.1. Calculation 
Calculation is carried out by 1 t prepared mortar.

9.4. Plastering

Before you start plastering, brick on the walls must be clean, and the fugue concave to better place mortar on the wall. Special attention should turn to concrete surfaces, which previously must be well cleaned and rare streaked cement milk. 
When plastering the walls of concrete and slag-concrete blocks, walls previously cleaned from the connectors eject unnecessary excess material, and the whole area well sprinkle with rare cement milk. 
Before plastering the walls of durisol blocks it is necessary to seal all joints cement mortar and the whole area sprinkle with rare cement milk, so that the horizontal and vertical joints do not see. 
All required materials must be masons adopted in the immediate vicinity and in sufficient quantities.

9.4.1. Rough plastering - first layer 
It is very important in any way to plaster so as to achieve a desired, flat surface. The long precise examination confirmed the following experience:

• to obtain a flat surface first must be thrown onto mortar bar length up to 2 mi wide 15 st, 
• When the tape thus thrown onto little mortar hard, using level instrument check the quality of the plastered  surface, 
• in case of need throw more mortar until the level instrument indicates a satisfactory result.

9.4.2. Fine plastering - second layer 
Only after the first layer of dry mortar, the wall is a little wet and throw onto the sifted mortar which is a large flat calendar. When the fine layer of plaster little hard, final polishing is done by board (a calendar) with occasional wetting, and so until the surface becomes quite flat.

9.4.3. Calculation 
Accounting is done by t 1. The Unit cost to mean the following papers:

• preparation of mortar mechanically, by 
• development (erection and dismantling) and removes light movable scaffolding, 
• occasionally mixed mortar, 
• adoption of water for wetting the walls, 
• cleaning job after completion of work. 
For easy mobile ferry is considered to be the legs with the base. 
Open around which there trowels to 20 cm wide refuses is as follows:

• open up to 3 m2 does not refuse you, but their trowels can not calculate, 
• at the opening of 3-5 m2, deducted over the surface of 3 m2, and their trowels are not calculated separately, 
• at the opening of more than 5 m2 refundable surface over 3 m2, and trowels be calculated separately.

Open in the walls deducted in full. 
If you are trowels wider than 20 cm, then the excess over 20 cm is calculated separately by t 1, and opened rejected as it was above the trowels to 20 cm. 
  
10. PAINTING WORKS

10.1. General

Work must be conscientiously carried out and first-rate. On painted surfaces must not be familiar traces of brushes, or must be the spot, the tone has to be uniform. Prints stationery and the roller must be clean and sharp, and the texture may not know. Painted surfaces must not be to wipe or peel. 
Made a line must be all the same length, width whether horizontal, vertical, or hair. 
If there were some shortcomings in terms of material or surface to be paint, office workers, that is to raise awareness in order to remove these shortcomings. 
All necessary materials for preparation of fatty and lean colors, a variety of mixtures must be adopted by a  professional worker in the room where he will perform the job. Professional worker is required to do in addition to his professional work and the preparation of another color, coloring, and trial preparation of the surface for painting. 
If the work required at the scaffolding, should be set at the time, before the painting and is calculated separately.

10.1.1. Painting with lime color (painting color) 
Applies mostly to the new buildings, the destitute uncle and connective means (glue and soap). It is recommended where the mortar dried slowly, and waiting only to drying. Suitable for work in the winter, in spring and autumn, when the color slowly droughts.

10.1.2. Edit of the  normed values 
At the site where at the same time does not work more than 200 tons of time to increase the standard of 18%. 
Near the stairs (staircases, space, shorter, resting stone wall) to increase the standard time to 11%. 
To work at a height of 4 to 6 m (up to 4 m is considered normal) to increase the standard time to 11%. 
a) To work at a height of 6 to 8 m, when working with scaffolding, to increase the standard time to 18%. 
b) To work at a height of 6 to 8 m, if it works with the ladder increase the standard time to 25%. 
To work through the 8 m height, increase the standard of time for (working with scaffolding) 34%. 
Painting of the factory establishments where they immobile machines, etc. to increase the standard time to 25%. 
For repairs that are performed in some damaged parts of the 1.00 m2 piece standard time is increased by 15%. 
To work in departments to 3.00 m2 in new buildings, the time norm increases by 60%. 
When painting on the rough sand standard time and materials for the new wall and ceiling increase of 30%. 
At polishing (ironing) in the rough sand of time norms and standards on use of materials increased by 50%. 
When painting in tones more standard time and standard use of materials will increase: 
a) for the battle of two tons of 100%, 
b) for the third tone coloring, and each further still to 75%.

10.2. Oil painting (oil) paint wooden objects

Accounting is done by T as follows: 
a) at the window, measuring is carried out inside the mortar and plasters, width times height, and so given space, with double windows, multiply the coefficient 2.90. The bill entered the box, a box between the wing and window windowsill to 15 cm and 15 cm over the calculated difference in particular, according to the actual extent; 
b) for painting ribs, the wings and set is added to 5% of the actual surface of windows (without inflation with k = 2.90) measured with one hand for each frame separately, counting frame over the entire window in one direction, without whatever the number of wings, and especially foreign, and especially for the inner panels; 
c) with single window display (cattle) without borders  calculated width times height windows, measured from mortar to mortar (inner measure) and multiply the coefficient 1.45 regardless of the dimensions of the window and the number of wings; 
d) for windows with a single border, the calculation is as for single windows without border only is multiplied coefficient 1.60; 
e) for painting ribs in single window, the calculation is the same as for double windows, with the difference that counted ribs once; 
f) at the window with the wings on the wing, the calculation is done as well as in double windows in a set with what is multiplied coefficient 2.40, and the use of standard materials reduces to 20%; 
g) Glassed cheat code, the calculation is done as when the window. Part of that is not glassed (full portion) is calculated according to the actual colored surface; 
h) at glassed partition calculation is done of the actual surface, count on both sides (of the mortar and plaster), irrespective of set; 
i) at glassed display is the obtained from the surface measured outside and inside as follows: 
- Glass surface for up to 3 t 45% 
- Glass surface for up to 5 t 30% 
- The surface of 5 m2 over 25%. 
j) at the door with a full crew and border (border) is the common area with a door border  and it is added to the surface display. By the gate where there are decorative parts, sections with the outburst of more than 6 cm, the calculated profiles developed; 
k) with full eyelids curtains (shutter) and the door is the common area; 
l) code eyelids with wings (blinds) and fuffle (flowing) are taken  1.5 times for each colored area. 
If the irrigation glassed windows paint done for legitimate reasons, standard time will increase to 20%. 
Painting doors in two different tones, for painting, enameling and  standard time will increase by 25%. 
When painting doors, wings, where on one side a 3-5 fillings increases the standard time to 18%. 
From 6 and more construction will increase the time for the standard 25%. 
When painting with only the external side is valid for classification 1, 3, 4 and 5, and for the classification of 2 and 6 standard time is increased by 25%.

10.3. Painting with oil paint plastered area

Calculation per m2 really colored surface. 
Concrete at the window height is multiplied with the width of the side kit slotting, and for the side with the pages (profiles) ribs, busy is 1.5 times the surface and sides. 
For painting the fat walls, making linkrusta, Teran, skin, mermera and so it really painted surfaces. 
Drawing lines and the gap in the front work is measured by m '. 
For painting concrete window (calculation of the surface by tac. 2) applicable standards as well as in carpentry, and classification of 201, 202 and 203, with what will be: 
a) for the side with the pages (profiles) to increase the standard varemena for 50%; 
b) to side with the kit slotting (kitfalc) increase the standard time for 30%; 
For painting the walls of fat, making linkrusta, Teran, skin, marble and the like, to a height of 1.80 m, is considered to be normal, with what will be: 
a) made to the surface at a height over 1.80 m, increase the standard time for 10%; 
b) to the surface in the stair, painted at a height over 1.80 m, increase the standard time to 15%.

10.4. Painting with oil paint of the iron items

Calculation of measures iron doors, windows, partitions and windows is carried out as for wood. At iron grid, doors (gates) fence, the calculation is divided into four groups as follows: 
a) with simple (easy) to create vertical and horizontal bars is the one-sided 
area; 
b) by creating a richer with horizontal and vertical bars, and by some decorative elements, 
is the double area; 
c) code to create a rich style of a leaf, meander, and similar ornaments filled with a lot 
Field 1.5 is the bilateral surface; 
d) with woven wire fence with holes of 4 cm is the 1.5 mutual surface. 
For metalworkers to take really colored surfaces. 
For the radiator is the height times width times ribs two sides times the number of ribs over 25%. 
When painting is the pipe size envelopes. 
When painting windows factory takes 1.5 times the common area. 
Calculation of standard time: 
a) at sheet metal  painting the roof with a tilt over 40o, increase the norm of 20%; 
b) by painting sheet metal  wreath, shed and other out up to 1 m, to increase the standard time for 
50%; 
c) at painting metal hanging gutter, drainage shuttle, sheet metal on the windows, standard 
time at position 403 increased by 75%. 

11. GRAVEL ROAD

11.1. General Provisions

Since the upper layer of the most important part of time and because of it depends on availability, quality and duration times, and therefore, and maintenance costs, that it should endow the maximum attention in the preparation. 
In the case of making grovel road  as a basis for modern roads, and the distribution of rolling grovel is carried out by the technical regulations that can contribute to or indicate the report. 
Procurement of materials is done by temporary technical regulations for the procurement of stone materials in gravel roads. 
Development of the lower consumption of roads is done by temporary technical regulations for the Earth. Clay Plan should previously processed, packed or rolled, and that in the highest regard no deviations greater than ± 3 cm. Works on the drainage below the machine should be completed before starting making roads.

11.2. Digging the bearing cover

Digging and planning of the base for background on the road is carried out according to the adopted type. The embankments are digging of the base works because it is determined that the embankment well charged, or constrict. The base should be making by pattern, with cross-slope as would have finished in time, and this is done in the same way as in cutting and embankments. Then he made light rolling by roller of 3-4 t weight, or greater weight rollers if you do not dispose of light rollers. If that happened to the base more Excavation, then this excess has to fill in stone. 
If you are at rolling of the base appear sink, then it is filled with earth excavated from the base and rolling continues. 
Milling of the base performs the cross up to 5 times the same footsteps, and the order that is proposed for the rolling of road. Underlay should be rolling in to keep the average concentration profile if this breaks down, it needs to be corrected by adding the country and rolling. 
About the beginning of the excavation, planning and rolling of the base decide purchaser agreed bodies and business organizations.

11.3. Stone background

The background to this is by type. To create a stone surfaces brings the stone with the figure, and bigger pieces of the breaks. Foundation stone for the strength of 20 cm to 5 m2 surfaces should be approximately 1.2 m2 figurated stone (without deduction of holes). Stones for the rough-adjust to the pass pyramidal forms and sets the administrative, tight , in good relation one to the other, with the base below a peak above, so that the land - bed - cover completely, without a hole as far as possible. From such a cornered and unflat stone surfaces, it can not be a rock hand draw. Then the peaks of stone surfaces bulging refuse, and holes suitable stones carefully meet and fixed. 
Since mostly stones and unflated, underlay the stamp down pestle, weight 16-20 kg, and each stone, then the background to a layer of well strength 3 cm, or stony sandy material (small stone, sand, gravel). This layer birch driving into broom in the cavity to fill the background and get the average time profile, according to the adopted type. Impress connecting material water comes into consideration only when suitable land (which is not solvent or softness of water).

11.4. Gravel Distribution

Prior to the start of distribution,it must be all made by the preceding paragraph of these regulations. Gravel distribution is done in layers of 6-12 cm. Usually gravel is spreaded and should be in in layers 8-10 cm, since at higher power there is a risk that the gravel is  uneven rolled, which causes the waves and bumps. For  gravel road layer 15 st in the rolled condition should roll two layers of gravel, and roadway class strength of 20 cm, three gravel layer, a layer of strength in the forward mentioned limits (which depend on the type and strength of stone). 
Coves and irregularities that occur during rolling is also filled with gravel by the same dimensions and quality, but very small stone 1 -3 cm, and since the previous rolled and corrugated metal rake furrow.

11.5. Rolling of the road

It should be at a moderately humid weather. Dry at the time and a safe land, in order to speed up work and for greater security against gravel movement and increase the internal stresses, should be with adding water. At gravel (and connecting material) required amount of water is usually 300 liters. When uncertain soil (clay and forests) are not watered (or adding a little water) to avoid base softness. By frost do not dare roll. 
Roads times should be steam or mechanical rollers 10-15 tons, or 15-20 tons, with karsnog limestone and roller 8-10 tons. With the rolling starts from the edge toward the middle of the curtain, and gradually by the entire width of the curtain gravel, speed of 3-4 km / h. 
Follows the journey of the roller should coincides with the previous 1 / 4 to 1 / 3, the cylinder must not follow in the footsteps of return. In order to obtain a good, solid and even in roads, should be good all the time while the skeleton gravel each other tightly and do not connect until they form a well compacted and it is possible to level surface. By such a surface car filled with water for water not show traces. Then the second layer is applied gravel and if this layer is the one who has to receive the traffic, i. e. , the final layer, then adds a binding material. In order to achieve reliable bearing gravel and what better tightness, no one may take more connecting material than is necessary. Too early or overtime adding connecting material has resulted by displacement of gravel underneath the roller. As the benchmarks that the well-rolled metal is used with metal assay of 4 cm from the same material as the gravel layer, when such a stone laid on the rolled metal, before the last wheel roller, on the pressure at the roller rolling successfully completed should be crack in the dust . If the stone does not crack in powder, or stamped down in gravel surface, rolling should be extended. Number of crossings is not the roller benchmarks for rolling gravel of the curtain, or is required, because the rolling sea, in any case extend until gravel shutter is not completely rolled. 
Prior to the traffic, it can be - which is not mandatory - in order to protect against shock road funds in road to cover another layer of 0.5 to 1 cm strength clean, sharp sand or small stone. Further compactness is achieved through traffic, which cavity in road reduced the minimum measure.

11.6. Roadway without foundation – macadam

Road, on the Mak-Adam – gravel road no stone surfaces - will be done only in those cases when there is no good for the stone or stony soil. 
Digging of the base for macadam is to be made the same way as it is for August and a surface, only one digs deep shoal, according to types, it also should be careful. 
Power of the curtain macadam is 25 cm, and at stony soil of 20 cm. It is built of three layers so that they, by impalement, the amounts specified thickness forward. For macadam is used as gravel, and pebbles, so what are for anticipated, largeness under the regulations for procurement. 
It is recommended that the lower class this road construction of larger, softer gravel, diameter 6-8 cm, and the upper layer of harder gravel 4-6 cm. 
Rolling macadam road is done as well as in road with a gravel surface. Lower layers must not be roll up to the end, to achieve better connections with the top layer.

11.7. Quality materials

For construction and maintenance on gravel road, as well as objects used in them are refracted stone, gravel, stone small, river pebbles and sand and binding material.

11.7.1. Refracted stone

Refracted stone called the stone obtained by mining and destruction by handspike, wedges and mallets. 
Refracted stone used for masonry objects, making the pavement and walls for security systems, especially for the production of foundation and fill holes in road deeper than 25 cm. 
Stone is prepared according to the size of the invoice from stones more or less strength, according to what is in use more economical for certain shares of times with respect to transport distance. Exclude the unhealthy, dilapidated stone and every stone on the volatile frost. Fixture on the rock pressure in dry able to bricklaying work must be greater than 700 kg/cm2, with arches min. 1000 kg/cm2, at the foundation stone for a min., 800 kg/cm2, when the pavement such as gravel, broken stone min. 1200 kg/cm2; it is, , as well as other technical features that they want, are for anticipated. Box-size stone for the foundation must not less than 10 cm h 20 cm. For parts of the terms of the strength of waste. 
The stone is taken from the quarries that were approved for work, and as result of the pre-conditions. 
If the stone from the quarry supplies for which there is no established data on quality, should be examine in some well-known Institute for testing materials, which will be submitted three sample size stones 16 cm h 16 cm h 16 cm with information about the quarry. 
Delivery of the stone is to be made in all by invoice, and these regulations. Stone should be delivered in all the matches given the quality. In the event of a dispute about mechanical or technical features can be made on his examination in a institute for testing materials.

11.7.2. Gravel

Gravel is used for road layer. 
For harder or lively traffic, average 300 to 5000 tons per day, taken in the Borders economy gravel road stone that can resist such traffic and which is what creates less dust. Stone must be healthy, great strength to the pressure and impact, that is a little wears out and crush that absorbs little water and it is steady at frost; not dare to rip a knife or difficult, must be a clear sound, and tough, sharp edge this gravel not must be crack under the pressure of thumb. Strength on the pressure in dry state must be at least 1400 kg/cm2, wear the shuffle max. 16 cm3, wear brim with fire simultaneously. 14%, absorption of water simultaneously. 2%. As a particular stone and steady with a firm connection is valid: granite, gabbro, kvarcporfir, porfirit and so eventually stones, quartz and sandy quartz . 
For easy transport, on average up to 300 tons per day, is used within the limits of cost-effectiveness of this road stone medium strength, but in any case, a healthy and stable in frost, they are, for example, more types of limestone and better types of sandy. They are, with regard to large sites and the cost of Shipping, with us for now most often used. Strength on the pressure in dry state at this stone must not be less than 1000 kg/cm2 and in proportion to the other mechanical and technical characteristics, with the proviso that guaranteed his steadfastness in the frost, this is in any case, are for anticipated. For parts of the terms of the strength of waste; search is exquisite, healthy, steady on the limestone frost. On the stone that has olivine and iron oxides should be special attention in terms of the stability of the frost. The stone, which contains more granular measure carbon as: calcite, aragonite, dolomite mineral, and sulfate, as: gneiss, anhidrit, mineral serpentine, zeolite and clay minerals: biolit and muskovit - in no case does not come into consideration for the gravel. Can not be used with ingredient stone with clay, as well as material from the surface layers, obtained by opening a quarry. 
Gravel can be crushed bronze machine or manually. It must be with possible sharp rand, but square shaped. Largeness gravel as a rule amounts to 4-6 cm for the creation of new roads, as well as for the distribution of new layers, 8-10 cm thick on old streets. Exceptionally, for very hard rocks, allowing the development of gravel largeness 3-5 cm, which is particularly provided are for. When repairs, as well as in gravel road, which will not be good, used metal 1-3 cm for repairs, and finish. By the size of gravel must be even, that is carefully sifted and Order. Laminated metal is not livable. Must not be contaminated organic ingredient; unrelated clay ingredients must not contain more than 2% by weight. In preparing the water is strict control of dimensions, shape and strength gravel and the general strict controls during acception.In  respect of the established mechanical and technological characteristics of gravel should act analog to. 5 and 6 of these regulations, with what will be the Institute for Testing Materials submitted in addition to 3 cm cubes 16 h 16 st h 16 cm, even 30 kg of finished gravel.

11.7.3. Stone (split)

If you are anticipated to be over gravel road set as modern in August, prepared on the total amount of gravel even up to 20% stone split, 1-3 cm, from the same types of gravel, which is used for filling holes and that stamp over the upper layer of gravel. For all splits applies what is said to metal in terms of quality and mechanical and technological tests. Stone splits must be separately figured. Splits of 1-3 cm can be saved for regular maintenance of roads as backup material.

11.7.4. River pebbles

At places where it is difficult to supply metal may be for repair and maintenance of roads using sturdy mountain and river pebbles. Gravel should be natural mixed various largeness, the smallest grains 1 cm, and the most large 5 cm, with a maximum of 20% sand and stone materials smaller than 1 cm, without a clean country and the organic ingredients. If you can not find a natural gravel mixture upper scale, then he must sift. In this sifted  gravel should be 25-35% of 1-3 cm, and 65-75% grains of 3-6 cm. sifting gravel is not carried out on the road. Mountain pebbles should match forward prescribed largeness and should be in mine sifted. 
If the mountain and river pebbles larger, then larger pieces to crack of prescribed largeness. For this type of gravelcan be used and scree from rivers and streams, but only if you come from illicit type of rocks by the attitude of 10th Metal saved from river stone may have a big drawback, we all scree are not the same strength, and the metal thus obtained unequally spends on the road and this spoils quickly. Therefore, this metal is used only when the second material can not be found, or it is a very expensive buy. Does not allow the use of gravel from weak and decay rocks, and t. etc.

11.7.5. Binding material to fill holes in stone surfaces

For this material is taken to scrap stones 0-4 cm, which is in the preparation of surfaces receive, then gravel, sand, slag, splits than Dilapidated rocks and similar material, but that water is not just mud.